QUESTION  DRA-TCR-TCAP-PSEP-3.1:

  - Estimating assumptions are provided in Appendix D of Sempra’s Amended Testimony.   Please provide any supporting workpapers, assumptions, justifications, or any other evidence supporting the following costs in the detailed cost estimates:

- Nitrogen ($.19 per SCF)

- Temporary pig launcher/receiver ($25,000 each)

- Hydrotest water ($19 per bbl)

- Hydrotest water disposal ($55 per bbl)

- Baker Tanks ($1,600 per day)

- Vacuum Trucks ($5,000 per day)

- Water pump and Filter ($486 per day)

- Misc. materials (5%)

- All labor unit costs in section 2, Construction

RESPONSE  DRA-TCR-TCAP-PSEP-3.1:

As stated in Response SCGC-4.4.1:

“Based on the preliminary nature of the pipe replacement cost estimates and the minimal engineering, operational planning, and project execution planning that has been done, per the AACE classification the cost estimates developed for the Pipeline Safety Enhancement Plan can be considered slightly better than a Class 5 Estimate.”

Note: the same statement can be applied to the pipeline hydrotest cost estimates provided by SPEC Services

Per AACE Guidelines, a Class 5 cost estimate is defined as having a level of project definition of 0-2% and typically uses stochastic or judgment as the method of estimating.  The hydrotest cost estimates can be considered  Class 5 estimates and were based on analogous and parametric estimating techniques, using historical costs of projects that were completed for numerous clients of SPEC Services. These projects were completed by energy-type companies, on projects with similar scope. As these estimates were compiled in a short amount of time, some exact costs were not available and judgment based, order of magnitude numbers were used.

    - The Nitrogen cost per SCF includes the cost of nitrogen as well as labor costs associated with the sub-contractor. The sub-contractor work includes purging technicians, truck drivers, mobilization/demobilization, etc.

    - The temporary pig launcher/receiver unit cost includes pricing for material used to construct the launcher/receiver (such as pipe, valves, and fittings) and the labor cost for the fabrication and installation of the pig launcher/receiver.

    - Hydrotest water unit costs include average direct pricing for the water and costs associated with filling the pipeline with the hydrotest water.

    - Hydrotest water disposal unit costs include costs associated with treatment of contaminated hydrotest water and were developed through conversations with water treatment vendors and review of past projects of similar scope.

    - Baker Tank unit costs include daily rental fees, mobilization/demobilization costs, labor costs associated with the operation of Baker Tanks during the pipeline filling and discharge, and vapor control system and tank cleaning costs.

    - Vacuum truck costs include the direct cost for the vacuum truck, fuel charges, and labor costs for a driver and operator to handle and transport pre and post hydrotest water.

    - Water pump and filter costs include direct rental costs and the cost of power or fuel to operate the pump.

    - The miscellaneous materials are included in estimates as a cost factor, but include cost estimates for air compressors, pigs, valves, fittings and other construction disposables. See Note 10 on page D-2 of the Amended Testimony.

    - Construction labor unit costs include test technicians, welders, helpers, pipe fitter and associated labor required to complete the hydrotest work. The hydrotest work includes nitrogen purging of the pipeline, excavation for installation of temporary pig traps, cutting of existing pipeline, water fill, performing the hydrotest, discharge of the hydrotest water, drying of the pipeline, and tie-ins for reactivation of the pipeline. Labor costs were developed via past projects of similar scope.

QUESTION  DRA-TCR-TCAP-PSEP-3.2:

  - Estimating methodology is provided in Appendix D of Sempra’s Amended Testimony.   Please provide any supporting workpapers, assumptions, justifications, or any other evidence supporting the following elements of the detailed cost estimates:

- Types and levels of contaminants in the effluent water from a hydrotest,

- Requirements for onsite pretreating of waste water following a hydrotest,

- Water pretreatment methods and costs,

- Whether the temporary pig launcher/receiver also provide the functionality of  test heads and/or test caps,

- Reason to limit the number of Baker Tanks per test to ten,

- What is included in SCG Labor/Inspection labor rate?

- Derivation of the three SCG Labor/Inspection labor rates,

- What is included in “Planning/Design/Engineering/Coordination/Procurement” labor rate?

- Derivation of the 5% “Planning/Design/Engineering/Coordination/Procurement” labor rate,

- ROW, permit costs, and environmental monitoring costs – where are they included in the estimate?

- Derivation of the 20% contingency rate?

- The reason for a higher 30% contingency rate for smaller projects.

RESPONSE  DRA-TCR-TCAP-PSEP-3.2:

- The costs included in the estimates for treating the hydrotest water are based on an average treatment cost for hydrocarbon based contaminated water.  In order to refine this cost, actual testing would need to be completed to determine whether other, non-hydrocarbon based contaminates may be contained within the pipe; potentially altering the basis of the estimate.

- The estimate assumes that there is no on-site pretreating of the hydrotest water.

- See Response DRA-TCR-TCAP-PSEP-3.2(b)

- The function of temporary launchers and receivers are similar to test headers.

- The maximum number of Baker Tanks was set to 10 to limit the construction work area to a reasonable size. Hydrotest water is temporarily stored in Baker Tanks before it is to be transported to a site for filtration and cleaning prior to disposal. The estimates assume Baker Tanks (500 BBL capacity) will be positioned at the end of each hydrotest section to collect water after each hydrotest. For each Baker Tank there will be a dedicated vacuum truck collecting water for disposal.  This quantity of tanks assumes dewatering and disposal can occur simultaneously at a comparable rate. Water disposal locations were assumed to allow for ten round trips per day for each vacuum truck. The estimates assume a 1-hour round trip, contaminated water, and a disposal fee.

- The SCG Labor/Inspection costs cover construction management and field inspection

- The same company labor/inspection factors that were included in the pipe replacement cost estimates were also used in the hydrotest cost estimates.  These factors were agreed upon by subject matter experts knowledgeable of pipeline project costs and take into consideration that the company labor component of a project accounts for a relatively smaller percentage as the overall project scope and cost increases.  The following direct costs were examples used to determine the basis and closely resemble historical replacement project direct costs:

| Project Cost | Company Labor | % |
| --- | --- | --- |
| $ 350,000 | $ 35,000 | 10% |
| $ 2,000,000 | $ 90,000 | 4.5% |
| $ 10,000,000 | $ 400,000 | 4.0% |
| $ 32,000,000 | $ 800,000 | 2.5% |

- Activities considered in this cost category include project engineering and design, review and approval of test procedures, and data analysis.

- The 5% factor used represents a reasonable estimate of the going rate for such engineering services.

- The hydrotest estimates do not include costs for right-of-way acquisition, construction permits, or environmental permits (see item 7(a) on page E-2 of the testimony).

- See Response DRA-DAO-01-5

- See Response DRA-DAO-01-5