QUESTION 1:

Regarding Figure V-3 (Sempra testimony, p. 72), please indicate the milepost of the rupture on the 18-inch pipeline, and the milepost of each of the ASV's that closed spanning and isolating the ruptured segment.

RESPONSE 1:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

Approximate rupture location was at Milepost (MP) 28.

ASVs closed at MP 20.81 and MP 30.48

QUESTION 2:

Please indicate the milepost where the indicated pressure (the red line in Figure V-3) was taken on the pipeline.

RESPONSE 2:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

Mile post 20.81.

QUESTION 3:

On page 73 explain the term "near-full rupture" related to the pipe event. Please provide any photos of the ruptured pipe.

RESPONSE 3:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

The term “near-full-rupture” was used because the pipe was not completely severed to the point of being two separate pipe ends.  A portion of the bottom of the pipe remained intact. See attached photos.

QUESTION 4:

Please provide full specifications of the ruptured pipe, including but not limited to the pipe grade and pipe thickness.

RESPONSE 4:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

Pipe ID: 17.5-inch

Pipe grade and wall thickness:  X50 @ .25” wt

Pipe date of operation:  12/1/1944

Pipe break dimensions: 61” L x 18”

QUESTION 5:

What was the pipe's MAOP for the segment shown in Figure V-3?

RESPONSE 5:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

MAOP: 650 psig

QUESTION 6:

For the pipe section that ruptured, what does the operating pressure of approximately 600 psig shown in Figure V-3 equate to as a % SMYS?

RESPONSE 6:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

SMYS:  Approximately 43.2% at 600 Psig.

QUESTION 7:

For each year 1990-2010, please provide SoCalGas’ and SDGE’s (separately): 1) forecast for ratemaking purposes and 2) actual recorded results, for each of the following:

  - Miles of transmission pipeline inspected via Direct Assessment

  - Capital and O&M expenditures (separately if available) for Direct Assessment

  - Miles of transmission pipeline inspected via In-Line Inspection (“smart pigging”)

  - Capital and O&M expenditures (separately if available) for In-Line Inspection

  - Miles of transmission pipeline replaced

  - Capital and O&M expenditures (separately if available) for pipeline replacement

RESPONSE 7:

SCG/SDG&E and TURN held meet and confers on: 1/27/12, 3/1/12, and 4/26/12. During these phone conversations, it was agreed that in lieu of the forecast amounts, SoCalGas/ SDG&E would provide the authorized settlement amounts from the rate proceedings in response to this data request.

a.1)	Authorized Miles of Direct Assessment (DA) inspection - There were no authorized amounts of miles to be inspected via Direct Assessment in the rate proceeding settlements.

a.2)	Recorded DA miles inspected - Table 1 shows the mileage of transmission pipeline inspected within the transmission integrity management program (TIMP) by both External Corrosion Direct Assessment (ECDA) and Inline Inspection (ILI) methods for both utilities.

Table 1

SoCalGas and SDG&E

Miles of Transmission Pipeline Inspected (TIMP)

ECDA and ILI (miles)

| Assessment Type | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SoCalGas - ECDA | 0 | 2 | 49 | 42 | 43 | 25 | 27 |
| SoCalGas - ILI | 181 | 262 | 597 | 282 | 71 | 182 | 524 |
| SDG&E - ECDA | 0 | 2 | 1 | 86 | 31 | 10 | 5 |
| SDG&E - ILI | 0 | 0 | 0 | 0 | 0 | 0 | 30 |

b.1)	Authorized Expenditures for DA - Capital and O&M - Table 2 shows the authorized funding levels for Pipeline Integrity through the applicable ratemaking mechanisms: 2004 Cost of Service (COS) and 2008 General Rate Case (GRC).  These authorized amounts include pipeline ECDA, ILI, and other inspections, repairs, and TIMP related replacements as well as project-specific and program-level costs, such as policy and program development, data analysis, and training.

Table 2

SoCalGas and SDG&E - Authorized TIMP

O&M, direct shared and non-shared

Capital, fully loaded

(Thousands, Nominal$)

b.2)	Actual Recorded DA – Capital Expenses –

A complete pipeline inspection, be it via ECDA, ILI, or another method, requires a number of activities to be performed before the inspection is considered complete.  These activities are designed so that a segment is properly analyzed and necessary integrity requirements are appropriately applied.  After the inspection has been performed, follow up analysis is performed to confirm that the resulting inspection data is reliable and accurate and that the appropriate repair and mitigative measures are completed.

Without drilling into individual work order accounting and conducting extensive activity-based analysis, it is not possible to provide a detailed activity-based accounting for the associated expenses for each specific assessment method.  In lieu of detailed activity information, we provide in Table 3 the capital expenses for the Integrity Management Program for SoCalGas and SDG&E.

Table 3

SoCalGas and SDG&E

Capital Expenses for Integrity Management Program

(Thousands, fully loaded, Nominal$)

| Capital - Actual | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SoCalGas - Capital | $27,742 | $35,560 | $37,229 | $42,898 | $30,207 | $42,794 | $66,554 |
| SDG&E - Capital | 0 | 0 | 0 | $343 | $789 | $-1 | $1,843 |

Actual Recorded DA – O&M Expenses –

Similar to the Capital discussion above, a discrete accounting of O&M expenditures for a particular assessment method is not readily available and would require extensive analysis at the work order level.

In lieu of detailed activity information, the summary of annual O&M expenses for the integrity management program is presented in Table 4.

Table 4

O&M Expenses for Integrity Management Program

SoCalGas and SDG&E (Thousands, Nominal$ excluding V&S factor)

| O&M - Actual | 20041 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SoCalGas – O&M | * | $5,205 | $10,961 | $13,150 | $11,777 | $14,295 | $22,583 |
| SDG&E – O&M | * | $499 | $941 | $2,085 | $2,262 | $736 | $1,076 |

1- Expenses for 2004 and are not included because the accounting practices in place during that time did not allow the Transmission Integrity Management Program values to be separated and reported.

c.1)	Authorized Miles of In-Line Inspection (ILI) - There were no authorized amounts of inspection miles via In-Line Inspection in the rate proceeding settlements.

c.2)	Recorded ILI miles Inspected - Please see response provided in Question 7(a.2)

d.1)	Authorized Expenditures for ILI - Capital and O&M - Please see response provided in Question 7(b.1).

d.2)	Actual Recorded Expenditures for ILI - Capital and O&M - Please see response provided in Question 7(b.2).

e.1)	Authorized mileage for pipeline Replacements - There were no authorized amounts of pipeline replacement miles in the rate proceeding settlements.

e.2)	Miles of Pipeline Replaced - Tables 5, 6, and 7 shows the miles of pipe replaced by year and the annual expenses incurred for pipe replacement.  The pipeline replacement work has been organized into three general replacement categories: TIMP Replacement, Routine Replacement, and Routine Relocation.  In addition, these activities have been further segmented by pipe diameter categories of “Less than 12”; 12” through 24”; Greater than 24”, and Multiple Diameters.  The Multiple Diameter category shows data for work orders that replaced pipe of two or more different diameters.  For these work orders, the accounting practices do not provide for a detailed breakdown of costs by individual diameter.  Negative values in these tables are primarily due to the timing of credits received for jobs that are collectible in nature.

Access to multiple data systems were required to provide the data for this request.  Plant accounting data was used to identify work orders where pipe was installed.  Additional analysis was needed to determine if the installation was for replacement or new business activities.  The financial data for these “replacement” work orders was then queried from the financial accounting data sets.

Many of these pipeline replacement projects span multiple years.  As such, the project costs may be accounted for over multiple years, with specific activity expenses applied during the year that the activity was performed.  The replacement mileage of a project is accounted for in the year the project is completed.  These accounting differences must be considered if efforts are made to determine a correlation between annual recorded costs and annual replacement mileage totals.

TIMP Replacement, Table 5 – The replacement of pipe in conjunction with pipeline integrity assessment activities.  This includes replacements associated with an integrity assessment such as to make a pipeline Piggable (valves and associated piping, Ells, bends, bypasses, crossovers, etc.), or assessment related repairs.  There were no TIMP-driven pipeline replacements prior to 2004.  There has been no pipeline integrity driven pipe replacement at SDG&E.

Table 5

SoCalGas - Pipeline Integrity driven Pipe Replacements

(Thousands, fully loaded, Nominal$)

Routine Replacement, Table 6 – This is routine, non-TIMP, pipe replacement work.  This includes pipe segment replacement due to a particular cause such as excavation or corrosion damage, due to natural causes such as earth movement, or to remove undesirable components, materials, or construction techniques.

Table 6

SoCalGas & SDG&E - Routine Replacement

(Thousands, fully loaded, Nominal$)

Routine Relocation, Table 7 – This covers jobs where there is a need to physically change the location of piping to accommodate government, private, or utility driven activities.  This includes replacement due to freeway widening, storm drain installation, or other property development.

Table 7

SoCalGas & SDG&E - Routine Relocation

(Thousands, fully loaded, Nominal$)

f.1)	Authorized Expenditures for Pipeline Replacements – The authorized expenditures shown in the response the Question 7(b1), Table 2 includes TIMP driven replacements.  The authorized expense amounts related to non-TIMP replacements, i.e., routine replacements and relocations, are not included and will be provided in a supplemental response by May 14th, 2012.

f.2)	Actual Recorded Expenditures for pipeline replacement - Please see response provided in Question 7

QUESTION 8:

Approximately how many manual shut-off valves are there on transmission lines in High Consequence Areas on the Sempra system?

RESPONSE 8:

Witness- Joe Rivera (Mike Bermel-Measurement Regulation Control Mgr)

Short Answer subject to caveats/interpretations below: 307 valves, which are all scheduled for conversion to RCV functionality in the PSEP.

There are approximately 4,000 valves servicing SoCalGas and SDG&E’s gas transmission system operations.  This includes valves of all sizes and all types of configurations (stations, mainline, interconnects, controls etc.)  A total of 337 of these valves are either remote or ASV functional in nature.  That leaves approximately 3,700 valves that are manually-operated on the transmission system.  Of these 3,700, however, a sub-total of approximately 671 valves can be used to support manual isolation of sections of high pressure DOT transmission pipeline in the event of a pipeline rupture (when used in conjunction with existing ASVs and RCVs). It is assumed TURN’s question is principally aimed at valves serving this sub-function.

The subset of these 671 existing manual DOT transmission pipeline valves to be specifically modified to support remote/automatic HCA isolation of pipelines pursuant to the PSEP is 307 valves.  These 307 valves, plus 20 new shorter-interval transmission valves and 40 backflow-prevention valves on distribution pipelines, constitute the valves required to isolate all SoCalGas/SDG&E HCA classified pipelines 12” in diameter and above operating above 30% SMYS and all HCA pipelines 20” and above in diameter operating above 20% SMYS.

The count of how many of these valves physically reside in HCAs would take additional time to review and can be provided, but the Class location in which the valves actually reside is not as important as the Class location of the pipeline segments they protect or isolate.  The PSEP approach was to use existing valve locations to protect Criteria HCA pipelines, where such protection could be generally achieved in intervals of 8 miles or less.  That total is 307 existing manual transmission valves.

QUESTION 9:

For what percentage of the miles of pipeline in High Consequence Areas has SoCalGas completed the federally-mandated initial inspections via 1) Direct Assessment or 2) In-Line Inspection?

RESPONSE 9:

Through 2011, SoCalGas has inspected 87% of the HCA mileage using ILI and ECDA.  In-line inspection has been used for 71% of the HCA mileage, and direct assessment has been applied to 16% of the HCA mileage.

QUESTION 10:

Please provide a copy of the data requests (only the requests, not responses) submitted to date by all other parties (including DRA and intervenors).

RESPONSE 10:

Attached are copies of all the data requests received to date.

Additionally, all responses to data requests received by SDG&E and SoCalGas received in R.11-02-019 are posted at SDG&E’s and SoCalGas’ websites under the webpages “Proceedings Before the California Public Utilities Commission (CPUC)” found at the links below.

http://www.socalgas.com/regulatory/R11-02-019.shtml

http://sdge.com/node/469