## Worksheet
| Applicant: | ESCO |  |  |  | Date: | 2009-01-01
| Host Customer: | Industrial Customer |  |  |  | Application No.: | XX-XXX
Instructions: | This spreadsheet determines if a proposed Level 3 (non-renewable) Fuel Cell system meets the Minimum Operating Efficiency eligilbility requirement of the Self-Generation Incentive Program. Applicants must provide documentation supporting all inputs including but not limited to system capacity, fuel consumption, waste heat recovery rate, operating schedule, equivalent full load operating hours and thermal load. See the 2008 SGIP Handbook for details of eligibility and documentation requirements. All yellow cells must be completed by Applicant/Host Customer.
Rated Net Generating Capacity = |  |  | 300 | kW | Full load net continuous rated capacity of the packaged prime mover/generator at ISO conditions.
Ancillary Generating System Loads = |  |  | 10 | kW | Any ancillary equipment loads necessary for the operation of the generator (e.g., fuel compressors, intercooler chillers, etc.) not accounted for in the Rated Net Generating Capacity.
Fuel Consumption Rate (LHV) = |  |  | 2178000 | Btu/hr | Provided by manufacturer or calculated from rated capacity and generator efficiency or heat rate specifications. Based on lower heating value of fuel.
Fuel Consumption Rate (HHV) = |  |  | 2418000 | Btu/hr | Provided by manufacturer or calculated from rated capacity and generator efficiency or heat rate specifications. Based on higher heating value of fuel.
Waste Heat Recovery Rate = |  |  | 480000 | Btu/hr | Recoverable heat as specified by manufacturer of generator or waste heat recovery unit at full load conditions. This is not total waste heat of the unit. The value provided should be supported by Generating System specifications (if packaged unit), Waste Heat Recovery System specifications, or engineering analysis of recoverable waste heat.
Month | Std Hours Per Month (hrs) | Generator Equivalent Full Load Hours per Month (hrs) | Capacity Factor | Generator Electric Output per Month (kWh) | Recovered Waste Heat per Month (Btu) | Thermal Load per Month (Btu) | Useful thermal energy output (Btu) | Fuel Input (LHV Btu)
Jan | 744 | 744 | 100% | 215760 | 357120000 | 358000000 | 357120000 | 1620432000
Feb | 672 | 672 | 100% | 194880 | 322560000 | 322200000 | 322200000 | 1463616000
Mar | 744 | 744 | 100% | 215760 | 357120000 | 289980000 | 289980000 | 1620432000
Apr | 720 | 720 | 100% | 208800 | 345600000 | 260982000 | 260982000 | 1568160000
May | 744 | 744 | 100% | 215760 | 357120000 | 234883800 | 234883800 | 1620432000
Jun | 720 | 720 | 100% | 208800 | 345600000 | 211395420 | 211395420 | 1568160000
Jul | 744 | 744 | 100% | 215760 | 357120000 | 190255878 | 190255878 | 1620432000
Aug | 744 | 744 | 100% | 215760 | 357120000 | 209281465.8 | 209281465.8 | 1620432000
Sep | 720 | 720 | 100% | 208800 | 345600000 | 230209612.38 | 230209612.38 | 1568160000
Oct | 744 | 744 | 100% | 215760 | 357120000 | 253230573.618 | 253230573.618 | 1620432000
Nov | 720 | 720 | 100% | 208800 | 345600000 | 278553630.9798 | 278553630.9798 | 1568160000
Dec | 744 | 350 | 47.04% | 101500 | 168000000 | 306408994.0778 | 168000000 | 762300000
Annual Total | 8760 | 8366 | 95.5% | 2426140 | 4015680000 | 3145381374.8556 | 3006092380.7778 | 18221148000
Minimum Operating Efficiency Eligibility = |  |  | PASS
P.U. Code 216.6 (a) = |  | 26.63% | ≥ 5% | TRUE | Public Utilities Code 216.6(a) & 18CFR Part 292
P.U. Code 216.6 (b) = |  | 53.69% | ≥ 42.5% | TRUE | Public Utilities Code 216.6(b) & 18CFR Part 292
Minimum Electric Efficiency = | Minimum Electric Efficiency = | 42.34% | ≥ 40% | TRUE | Public Utilities Code 353.2 and 379.6
Note on G13: This is the thermal load on monthly basis. The value provided should be supported by thermal load analysis. May be calculated from equipment ratings and/or historical fuel bills. Industrial or commercial process (net heat contained in condensate return or make-up water); heating application (e.g., space heating, domestic hot water heating); space cooling application (e.g., thermal energy used by an absorption chiller).
Note on C13: Forecasted generator electric energy output. Monthly values should be supported with engineering calculations of generator operation including system maximum and minimum rated loads, Host Customer Site load, Site operating schedule and accounting for scheduled as well as unscheduled maintenance.