Prepared by:

Energy and Environmental Analysis

(An ICF International Company)

12011 NE First Street

Suite 210

Bellevue, Washington  98005

Contact:

Rick Tidball or

Stu Knoke

T:  (425) 688-0141

F:  (425) 688-0180

ICF Report No. 20901A

Version A

Kitchen and Laundry DHW Controller for Lodging Facilities

Workpaper for PY 2009-2011

June 2009

Prepared for:

EDC Technologies, Inc.

Disclaimer

Southern California Gas Company has made reasonable efforts to ensure all information is correct.  However, neither Southern California Gas Company 's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service.  Moreover, Southern California Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

San Diego Gas and Electric Company has made reasonable efforts to ensure all information is correct.  However, neither San Diego Gas and Electric Company 's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service.  Moreover, San Diego Gas and Electric Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

Kitchen and Laundry DHW Controller for Lodging Facilities

| Information Submitted: |  |  | Workpaper – Kitchen and Laundry DHW Controller for Lodging Facilities (PY 2009-2011), ICF Report No. 20901A, June 2009 Attachments #1 – Gas Savings from Programmable Setback |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Submitted by: |  |  | Energy and Environmental Analysis, Inc. (an ICF International Company) |  |  |  |  |
| Date: |  |  | June 9, 2009 |  |  |  |  |
| Program Affected: |  |  |  |  |  |  |  |
|  | X | Express Efficiency |  |  |  | Energy Efficiency Grant Program (EEGP) |  |
|  |  | Process Equipment Replacement (PER) |  |  |  | Custom Process Improvement (CPI) |  |
|  |  | Efficient Equipment Replacement (EER) |  |  |  | Recognition Program |  |
|  |  | Business Energy Efficiency Program (BEEP) |  |  |  |  |  |
|  |  | Other (please describe) |  |  |  |  |  |

Revision History

| Revision No. | Date | Description | Author |
| --- | --- | --- | --- |
| --- | June 9, 2009 | Original release | ICF (S. Knoke) |

# At a Glance Summary

Measure data for cost effectiveness were developed for kitchen and laundry DHW control systems used in lodging facilities; including hotels, motels, resorts, and casinos (NAICS codes 7211).  Unitized cost effectiveness determinants are summarized below.  The first section of this table draws from data collected on 12 kitchen and laundry DHW controllers at 11 lodging facilities.  These DHW systems use small uncontrolled hot water boilers – generally between 300 and 3,000 MBtuh.  The average gas savings is about 4,400 therms per year per controller serving kitchen and/or laundry areas, as a result of the transition from baseline (standard) operations (using existing DHW systems) to the DHW controller on a programmable setback temperature schedule (controlled operations).  As per third-party energy conservation program agreements, the installed cost of the system is $1,500 per controller.  There is no additional monthly charge -- the kitchen and laundry DHW controllers are combined with DHW control systems for boilers serving the guest rooms for which a Continuous Commissioning® service charge of $1 per month per guest room is paid by the lodging facility.  Based on the annual gas savings shown, the cost of equipment and installation (and the total measure cost) is 4¢ per therm saved over the equipment useful life (prior to applying the net-to-gross ratio).

| Parameters | DHW Temperature Setback Controller |
| --- | --- |
| Average number of guest rooms served by kitchen and/or laundry area | 262 |
| Average boiler capacity (MBtuh/controller) | 1,266 |
| Annual operating hours | 8,760 |
| Average gas savings from standard operations to controller set at programmable setback temperatures (therms/year/controller) | 4,393 |
| Annual Energy Cost Savings |  |
| Annual energy cost savings ($/year/controller) | $4,173 |
| Measure Cost (MC) |  |
| Cost of equipment and installation ($/controller) | $1,500 |
| Annual cost to lodging facility ($/year) | $0 |
| Measure cost to lodging facility (¢/therm saved) | $0 |
| Payback |  |
| Years, without rebate | 0.4 |

# At a Glance Measure List

| Parameters | DHW Temperature Setback Controller |
| --- | --- |
| Summary of Key Parameters |  |
| Average gas savings from standard operations to controller set at programmable setback temperatures (therms/year/controller) | 4,393 |
| Annual measure cost to lodging facility ($/year) | $0 |
| Measure cost to lodging facility ($/therm saved) | $0 |
| Measure lifetime (years) | 15 |
| Net-to-gross (NTG) ratio | 0.80 |
| MDSS Measure Code |  |
| Application Code |  |
| Key Parameters for CEC Filing |  |
| Measure No. |  |
| Measure cost ($/unit) |  |

TABLE OF CONTENTS

Page

At a Glance Summary	v

At a Glance Measure List	vi

1.	General Measure and Baseline Data	1

1.1	Measure Description	1

Market Applicability	5

Terms and Conditions	5

Qualifying Parameters	5

1.2	DEER Differences Analysis	5

1.3	Codes and Standards Requirements Analysis	5

1.4	EM&V and Other Studies	5

1.5	Energy Rebated Base Description	6

1.6	Measure Effective Useful Lives	6

1.7	Net-to-Gross Ratios for Difference Program Strategies	6

2.	Calculation Methods	7

2.1	Electric Energy Savings Estimation Methodologies	7

2.2	Demand Reduction Estimation Methodologies	7

2.3	Gas Energy Savings Estimation Methodologies	7

3.	Load Profile	8

4.	Base Case and Measure Costs	9

4.1	Base Case Costs	10

4.2	Measure Case Costs	10

4.3	Incremental Measure Case Costs	10

References	11

List of Attachments	12

Appendix A.	Common Types of Domestic Hot Water Systems	13

Appendix B.	Gas Savings from Programmable Set-Back DHW Thermostat Controller	21

LIST OF TABLES

Page

Table 1.	Measure Cost	10

Table 2.	Variables That Effect Energy Use Relating to Hot Water Consumption	14

Table 3.	Test Dates for Calculating Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback	22

Table 4.	Test Results for Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback	23

Table 5.	Statistical Analysis of Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback	23

LIST OF FIGURES

Page

Figure 1.	Typical Kitchen and Laundry DHW System Consisting of an On/Off Type Boiler System with a Storage Tank	2

Figure 2.	Typical Kitchen and Laundry DHW System Consisting of an On/Off Type Boiler System with a Storage Tank and Piping Loop	3

Figure 3.	Example of Load Shape for a DHW Boiler System Serving Kitchen and Laundry Areas at a Lodging Facility	9

Figure 4	Modulating Boiler with No Storage Tank	16

Figure 5.	Daily Recorded Delivery Temperatures for an Instantaneous or On-Demand Type System	17

Figure 6.	Modulating Boiler with Storage Tank	18

Figure 7.	Charts for Modulating Boiler with Storage Tank	19

Figure 8.	Standard Commercial Water Heater with Integral Tank	20

# 1.	General Measure and Baseline Data

## 1.1	Measure Description

This workpaper addresses the gas savings that can be expected as a result of an energy efficiency measure for controlling kitchen and laundry domestic hot water (DHW) systems in the lodging industry, including hotels, motels, resorts, and casinos.  This measure includes two process improvement components:

- Set-Back DHW Thermostat Controller – This energy savings measure is to install a programmable set-back temperature controller on the DHW system.  A programmable set-back controller saves energy by lowering the DHW thermostat setting during times of low DHW usage.  The controller can be programmed remotely or on-site, based on data collected from a variety of sensors and a datalogger installed on-site.  The data can be retrieved remotely or on-site.  The DHW system will provide the required hot water temperature to the kitchen and laundry areas, but with significant energy savings.

- Continuous Commissioning® – Continuous commissioning maintains long-term energy savings by using ongoing monitoring of energy consumption and system parameters with follow-up commissioning, as needed.  Without continuous commissioning taking place, new system problems, inefficiencies, and malfunctions go months without being detected and repaired.  Hence, continuous commissioning is an essential part of the long-term gas savings from DHW thermostat controllers.

Kitchen and laundry DHW includes only the hot water supplied to the kitchen and laundry areas.  The hot water is primarily used for commercial restaurant dishwashing machines and commercial clothes washing machines.  Applications of the measure to hot water systems serving the guest rooms of a lodging facility and public use in lodging facilities are excluded.  The general measure and baseline data for this energy savings measure is discussed below.

A typical equipment arrangement for these measures consist of a hot-water storage tank, a hot-water boiler which includes a circulation pump, and piping to supply the heated domestic hot water (DHW) to the kitchen and laundry areas.  More often than not, the kitchen and laundry DHW systems include a piping loop and a recirculation pump on the return line from the piping loop.

In lodging facilities in southern California, natural gas is used primarily for heating water for use in kitchens and laundries, for guest use, for public use, for swimming pools, and for spas.  A common arrangement is to operate a high-temperature boiler system to supply ~140 degrees Fahrenheit (°F) hot water to the kitchen area (primarily for dishwashers) and ~120 °F hot water to the laundry area.  To supply domestic hot water to the guest rooms, the lodging facility usually operates several separate DHW boiler systems at a moderately high temperature (110-120 °F).  Sometimes the kitchen and laundry hot water is drawn from the guest room DHW system and heated (or “boosted”) to the desired temperature.  Almost all dishwashers have integral booster heaters.  Water heating for public use, pools, and spas are often separate systems, but may also be tied into the guest room DHW system.

Some DHW systems serving kitchens and laundries have recirculating piping loops and some do not.  As a general rule, hotels have restaurants and kitchens, and motels do not.  If the lodging facility has a kitchen, then most likely it has a piping loop.  Motels with more than 50 or 60 guest rooms will most likely have a laundry facility.  If the lodging facility has a laundry area but no kitchen, then it rarely has a piping loop.

Figure 1 shows a simplified flow diagram for a DHW water system with no piping return loop.  Cold water (typically 65 °F) is drawn into the bottom of the storage tank when water is used in the kitchen or laundry areas, or into the boiler when it is operating.  The boiler provides hot water to the storage tank.  The on-off boiler comes on when the water temperature in the storage tank drops below its lower limit setting, and shuts off when the water temperature exceeds the upper limit setting.  During the busy part of the day, the hot water pipes leading to the kitchen and laundry areas are maintained at a temperature only a few degrees below the storage tank temperature.  After a few hours without drawing any hot water, the hot water pipes leading to the kitchen and laundry areas will approach room temperature.  Thus, the first few gallons of water drawn after a lengthy inactive period will be lukewarm, until the pipe refills with hot water.  In addition to the hot water used by the kitchen and laundry areas, the heat output from the gas boiler must overcome heat loss from the storage tank and water pipes to ambient.  Other hot water energy consumption includes crossover, water leaks at faucets and appliances, and water leaks in underground pipes.  The hot water consumption due to crossover and leaks are rarely known.

Figure 1.	Typical Kitchen and Laundry DHW System Consisting of an On/Off Type Boiler System with a Storage Tank

Figure 2 shows a simplified flow diagram for a DHW water system with a piping return loop.  The boiler system works the same as without the piping loop.  Here the recirculation pump operates all the time to maintain the loop to the kitchen and laundry areas at a temperature only a few degrees below the storage tank temperature.  In addition to the hot water energy consumption factors listed above, the piping loop required heat output from the gas boiler to compensate for heat loss from the piping loop even when there is no hot water use (called “standby loss”).

Figure 2.	Typical Kitchen and Laundry DHW System Consisting of an On/Off Type Boiler System with a Storage Tank and Piping Loop

Most lodging facilities have constant-temperature controllers that maintain the water temperature in the storage tank between the same two set points at all times.  The “dead band” between these set points is ideally 2-4 °F, but in poorly maintained systems, it is often as large as 10-15 °F.  The upper set point is commonly around 120 °F for DHW systems serving laundry areas, and around 140 °F for DHW systems serving kitchen areas.  The highest water temperatures used in kitchen and laundry areas is 145 °F.

This workpaper addresses the gas savings that can be expected as a result of an energy efficiency measure for DHW thermostat controllers serving kitchen and laundry areas at lodging facilities.  The energy-efficiency measure consists of the following stages:

- Sensors and dataloggers – The dataloggers receive up to sixteen temperature inputs (each records the minimum, maximum, and average temperatures during each half-hour period), four meter dataloggers which are programmable to read cumulative seconds when voltage is present or pulse counts from meters, with numerous data recording functions and intervals for all sensors.

- The boiler control – A programmable temperature control that consists of 336 temperature set points (one for each half hour of a weekly cycle).  There are four control relays which allow independent control of four heaters or stages.

- The communications link – All dataloggers and controllers are connected to a form of communication on the property which is either a direct link or a wireless link to a central point where data or instructions are passed to and from communications servers located at the DHW controller service provider.  All data are downloaded hourly or daily depending on the communications type.

- Data analysis – Incoming data is analyzed to look for anomalies in the control system and in the hot water system.  Control system problems such as control operation status, communication problems, and control component problems are problems for the DHW controller service provider to address.  Anomalies with the hot water system and other system inefficiencies are identified as problems for the customer to address.

- Presentation of data to the customer – Each client and property is allowed secure access to their data and analysis through the DHW controller service provider web site.  Clients and properties can use the data for historical reference, as a contractor interface, or for other purposes.  If the client elects to allow the service provider to collect baseline data of run times for controlling relays and gas valves, an assessment of actualized savings can be prepared.  Either the client or the DHW controller service provider can analyze any property data in detail to see up-to-date property data and operation graphs of temperatures and system run times for controlling relays and gas valves.  Clients and properties receive email or other notifications of anomalies identified during “manual” or automated DHW system analysis by the DHW controller service provider.  Once the problems are clearly identified, the customers generally make the recommended repairs.  When anomalies are not addressed, the DHW controller service provider elevates the concern to client management and the property owner.  This notification approach results in a very high success rate of correcting the anomalies.

The major benefit of the DHW thermostat control system results from its ability to record and analyze problems with the hot water system that have a direct affect on energy use and hot water consumption, i.e., hot water leaks, crossover problems, hot water system inefficiencies or problems like pump failures, and short cycling.  This benefit comes from having detailed knowledge of system performance, which allows the identification of the anomaly, and, since the DHW controller also serves as an on-line portal, the data are regularly transferred to a server where it is processed and analyzed.  The DHW controller service provider posts the hot water data online for review from anywhere the customer has internet access.  The DHW software also identifies equipment plumbing problems remotely and notifies the customer immediately in the event of operational problems such as water leaks, pump failures, heater malfunctions, and other DHW system failures.  This benefit of the DHW controller has primarily been proven through numerous field test studies performed over years of gas savings at multi-family residences.

A control system used in this manner for data logging can have a very large impact on overall energy use as most hot water system problems waste large amounts of energy and hot water, which will often go undetected or be masked by increasing operating temperatures to artificially “solve the problem”.  The net result of the DHW commissioning and control system is significant energy savings due to prompt (and correct) identification of the problem and due to prompt repair of the hot water system.

The DHW controller also allows the thermostat setting on the hot water boiler systems to be programmed at the 336 half-hour intervals in a weekly cycle to save energy, much as a programmable home thermostat saves energy by turning down the thermostat at night.  The ability to optimize temperature settings for adequate (but not excessive) hot water delivery during all consumption periods leads to greatly increased system efficiency.  When required, the DHW controller service provider can reprogram the 336 thermostat settings remotely to lower the storage tank temperature limits during times when the kitchen and/or laundry areas use little water.  Thus, the DHW controller reduces the heat loss from the tank and pipes and reduces the temperature of the hot water delivered to the kitchen and laundry areas by minimizing the water temperature in the storage tank.  Using the DHW controller, the storage tank temperature is highest during times of maximum hot water use (daytime and early evening), and lowest in the middle of the night.

### Market Applicability

The target market for this measure is lodging facilities with kitchens and/or laundries.  In this workpaper, DHW includes the hot water supplied only to the kitchen and/or laundry areas.

### Terms and Conditions

Only hot-water systems used primarily for kitchen and/or laundry domestic hot-water heating uses qualify.  Applications of the measure to hot water systems for guest rooms, pools, spas, and public use in lodging facilities are excluded.  The boiler manufacture’s name, equipment model number, input capacity of the hot-water generator, the output capacity or thermal efficiency rating of the hot-water generator, and year the lodging facility was built must be provided.  If more than half of the square-footage served by this controller is due to an addition to the lodging facility, then use the addition’s construction year.

### Qualifying Parameters

The minimum qualifying boiler capacity is 250,000 Btu/hr.  Smaller boiler systems serving kitchen and/or laundry areas are undersized.

## 1.2	DEER Differences Analysis

The DEER database does not contain a measure for kitchen and/or laundry DHW controllers for use at lodging facilities.

## 1.3	Codes and Standards Requirements Analysis

There were no specific codes and standards identified that addressed DHW controllers for kitchens and/or laundries at lodging facilities.

## 1.4	EM&V and Other Studies

Several EM&V studies have been performed that address DHW controllers for various applications, as listed below, but none were identified which specifically addressed kitchens and/or laundries at lodging facilities.

- Commercial Boilers, Workpaper for PY2006-2008, Version B, by Energy and Environmental Analysis, Inc., for Southern California Gas Company, Los Angeles, California, March 2006.

- Demand-Controlled Setback DHW Thermostat Controller Replacement of an Existing DHW Constant-Temperature Controller (Multifamily Residential), Energy Efficiency Workpaper prepared by Eric Kirchhoff, Southern California Gas Company, December 19, 2005.

- DHW Commissioning and Control System for Lodging Facilities, prepared by Energy and Environmental Analysis, Inc. (an ICF International Company), for Southern California Gas Company, Los Angeles, California, Version B, March 2008.

- Evaluation Measurement and Verification Report for the Gas-Only Multifamily Efficiency Program  #197-02, By Robert Mowris & Associates, P.O. Box 2141, Olympic Valley, CA 96146 Telephone 800-786-4130, rmowris@earthlink.net; For SESCO, Inc., March 2, 2004.

- Evaluation of the 2004-2005 Statewide Multifamily Rebate Program – Volumes I and II, Final Report for Program 1118-04; by KEMA; for The California Public Utilities Commission, San Francisco, California; Pacific Gas & Electric Company, San Francisco, California; San Diego Gas & Electric Company, San Diego, California; Southern California Edison, Rosemead, California; and Southern California Gas Company, Los Angeles, California; March 16, 2007.

## 1.5	Energy Rebated Base Description

The base case for the measure is a constant-temperature controller for the DHW system serving kitchen and/or laundry areas at lodging facilities.

## 1.6	Measure Effective Useful Lives

- Based on the CPUC Energy Efficiency Policy Manual recommendation for water heater controls, the effective useful life (EUL) is 15 years.  This EUL is applicable to retrofit and replace-on-burnout of existing thermostat controllers.  The realization factor on measure lifetime is, however, somewhat less than 100% because a small percentage of facilities will terminate their Continuous Commissioning contract before the end of the EUL.  The realization factor is the ratio of the total years of service of the installed controllers divided by the number of installed controllers.  There is minimal data on the long-term retention for lodging facilities, but there are data for multi-family residential DHW controllers.  EDC Technologies installed DHW controllers on 52 properties as part of a PG&E program established in 1994 at multi-family residential housing.  Only 16 contracts have been terminated to date, even though the terms of these contracts ranged from 6 to 12 years.  The reasons given for contract termination were one of four types:

- Did not reestablish contract at end of 10-year program (the controls were returned to EDC Technologies

- Existing owners cancelled contract

- Change of ownership canceled contract

- Converted system from boilers to individual water heaters

- If the controller is still in use, then the number of years of service for this analysis was assumed to be 15 years.  Based on this data, the realization factor for the EUL was 91%.

## 1.7	Net-to-Gross Ratios for Difference Program Strategies

The net to gross ratio is an estimate of free ridership occurring in energy efficiency programs.  Free riders are program participants who would have implemented an energy efficiency measure even if the energy efficiency program had not been offered.  The CPUC Energy Efficiency Policy Manual recommends a value of 0.80 for “All other nonresidential programs”, and, as such, this workpaper adopts its recommendations.

# 2.	Calculation Methods

## 2.1	Electric Energy Savings Estimation Methodologies

There are no electric-energy savings associated with this measure.

## 2.2	Demand Reduction Estimation Methodologies

There is no anticipated demand reduction associated with this measure.

## 2.3	Gas Energy Savings Estimation Methodologies

Lodging facility domestic hot water (DHW) systems consume energy in two distinct ways:  hot water for consumption, and standby losses.  Whenever DHW is drawn from the system, fresh cold water flows into the hot water storage tank, which is heated with a large hot water heater or hot water boiler to a temperature that will satisfy peak demand hot water use.  Consumption for kitchen and laundry areas requires temperatures ranging from 120 to 140 °F.  The amount of energy used to heat water for consumption is therefore directly related to the amount of hot water used in the kitchen and laundry areas, the efficiency at which the water is heated and delivered (which includes boiler efficiency and system heat loss), and the temperature rise required to heat the cold water to satisfy hot water needs.  See Appendix A for a description of common types of DHW systems.

If the kitchen and laundry DHW systems include a piping loop for hot water distribution, energy is also used to compensate for standby losses in the piping loop.  In order to provide hot water to every appliance and faucet in the kitchen and laundry areas, hot water is continuously circulated in the piping loop and returned to the hot water storage tank.  This distribution system incorporates a re-circulating pump that operates all the time.  Depending on the time of day and DHW consumption rate, energy consumption for the standby losses may be greater than the energy consumption for the actual hot water use.  Standby losses are primarily due to heat loss from the piping loop to ambient, which results in the return water continuously being reheated and staged for consumption.  Standby losses are a function of water temperature and flow rate, pipe size and material, length and configuration of pipe loops, insulation condition, air circulation around the pipes, and radiative heat loss.  Unlike the variables that affect hot water consumption, the standby loss variables are relatively stable.

DHW gas savings follow the installation of a new DHW system controller due to demand-controlled setback of the thermostat.  The gas savings vary greatly from one facility to another.  A calculation of gas savings at each facility would require many measurements and detailed engineering analysis.  The most direct method to determine gas savings at each installation is to calculate the gas use from measurements of the cumulative time in every half-hour period that the boiler operates (i.e., boiler gas control valve is open) made for at least a week to capture normal operational cycles.

Lodging facility DHW use varies through each day in a consistent manner.  Like the automobile driver who presses the accelerator in anticipation of an upcoming hill, or the electric grid operator who brings additional generating capacity on-line in anticipation of the afternoon peak daily load, the supply temperature of a DHW system can be lowered at night to save energy and raised in the early morning in anticipation of the daytime load.  Peak DHW use in systems serving kitchen and laundry areas at lodging facilities generally occurs between 6 AM and 11 PM; while peak DHW use in systems serving laundry only generally occurs between 9 AM and 6 PM.  Between midnight and 5 AM, there is normally no hot water use in kitchen and laundry areas.

As discussed in more detail in Appendix B, lowering the set point in a consistent daily pattern reduces the heat loss from storage tank and boiler, the heat loss from piping, the heat used for ready hot water for consumption, the heat loss due to cross-over and, when the system has a piping loop, the heat loss in the piping loop.  To determine the setback schedule for each lodging facility, the DHW controller system must continuously monitor system parameters such as the following:

- Cumulative time in each half-hour period that the DHW controller requests each boiler to operate (i.e., the boiler control relay is closed)

- Cumulative time in each half-hour period that the boiler operates (i.e., boiler gas control valve is open)

- Supply temperature (temperature of hot water at the exit from the storage tank to the supply lines)

- Return temperature, if any (temperature of hot water returning from the piping loop)

After these system parameter data are collected for a week, the DHW controller service provider empirically determines the new DHW controller setback schedule.  A week or two later, the system parameters are reviewed again, and the DHW controller service provider may readjust the DHW controller setback to achieve additional savings or to maintain proper water delivery temperature at all times.  As long as the system is operating properly, hot water of the proper temperature is delivered to the kitchen and laundry areas.  As soon as the system malfunctions, all parties are notified and repairs are made.

Gas savings data were collected on numerous controllers at lodging facilities in southern California in 2009.  As described in Appendix B, the expected energy savings in going from controlling to a constant temperature band (standard) to the programmed setback schedule (controlled) at lodging facilities is 4,393 therms per year per controller serving kitchen and/or laundry areas.

These energy savings resulting from proper hot water system operation are not, however, permanent in any sense.  In the months following the installation of the DHW controllers and dataloggers, new problems will inevitably arise:  switches will fail, valves will cease to open and close, mixing valves will start to leak, and boilers will cease to operate properly.  Without continually monitoring the data, the DHW system operator may need to raise the DHW maximum set point setting again to achieve the desired hot water temperature delivered to the rooms.  Long-term gas savings resulting from the hot water system operating at peak efficiency are accomplished only by continually monitoring the system data, a process known as “Continuous Commissioning”.  Without this continuous commissioning taking place, the new problems will once again go months without being detected and repaired.  Hence, continuous commissioning is an essential part of the long-term gas savings.  But even when the DHW system is not operating at peak efficiency, the controller will provide energy savings (and perhaps more than when the system is operating properly).

# 3.	Load Profile

This workpaper only addresses natural gas; therefore, no load profile is required per the energy policy manual.  However, Figure 3 shows an example of the natural-gas load shape for DHW boilers serving kitchen and laundry areas at lodging facilities.  These data were calculated by averaging run-time measurements from five actual boilers.  The standard load shape shows the boiler operating at low load during the night when no hot water is used and at much higher loads during the day when bedding and towels are being washed in the laundry area and dishes are being washed in the kitchen.  The controlled load shape shows almost no energy use at night, followed by a burst of usage to bring the hot water storage tanks back up to full operating temperature.  Daytime energy usage is reduced from the standard load as well.

Figure 3.	Example of Load Shape for a DHW Boiler System Serving Kitchen and Laundry Areas at a Lodging Facility

# 4.	Base Case and Measure Costs

In general, the incremental measure cost (IMC) is the difference between the new measure installed cost and the baseline installed cost.  The IMC should account for the expected useful life of the existing and new technologies.  The IMC depends on the activity type:

- Retrofit a working technology prior to failure

- Replace a technology at the end of its useful life

- Installation a new construction or major renovation

The DHW controller is a retrofit on working technologies prior to failure.  All installed DHW controller systems include the digital hot water controller, a communications interface (either wireless or hard wired), all sensors and control connections, and connection and setup to the DHW controller service provider server interface for monitoring and system operation along with a customer interface.

## 4.1	Base Case Costs

This measure is a “RET” or Retrofit type, so the base case costs correspond to the “do-nothing” option.

## 4.2	Measure Case Costs

Since no hardware is taken out of service, the measure cost is the cost of the DHW controller.  As per the third-party energy conservation program agreements with Southern California Gas Company and San Diego Gas and Electric, the price to install the DHW controllers on hot waters system serving the kitchen and laundry areas is $1,500 per controller (Table 1).  The installed price includes all costs incurred for the installation and setup of the control system.

There is no additional monthly charge for the kitchen and/or laundry DHW controller since the controllers are combined with DHW control systems for boilers serving the guest rooms for which a Continuous Commissioning® service charge of $1 per month per guest room is paid by the lodging facility.  This monthly charge pays for the communication connection, system monitoring, and controller equipment maintenance, upgrades, or replacements as needed for the DHW controllers serving the kitchen and laundry areas as well as the guest rooms.  The equipment (controllers, relays, modems, etc.) is usually replaced about every five years, and the firmware and software is upgraded much more frequently.  While control system problems such as control operation status, communication problems, and control component problems are covered under the monthly charge, problems with the hot water system and other system inefficiencies are identified as problems for the lodging facility operator to address.  Once identified, the lodging facilities are generally very prompt about making the needed repairs.

Table 1.	Measure Cost

| Parameters | DHW Temperature Setback Controller |
| --- | --- |
| Cost of equipment and installation ($) | $1,500 |
| Monthly charge ($/year) | $0 |
| Average gas savings from baseline operations to controller set at programmable setback temperature (therms/year) | 4,393 |
| Cost per Therm Saved |  |
| Annualized cost of equipment and installation (¢/therm saved over EUL) | 4 |
| Monthly charge (¢/therm saved) | 0 |
| Annualized total measure cost (¢/therm saved over EUL) | 4 |

## 4.3	Incremental Measure Case Costs

The incremental measure costs are the same as the measure case costs since the base case is equivalent to taking no action (i.e., the “do nothing” approach).

# References

- 2007 ASHRAE® Handbook, Heating, Ventilating, and Air-Conditioning Applications, Inch-Pound Edition, American Society of Heating, Refrigerating, and Air-Conditioning Engineers, Inc., Atlanta, Georgia.

- DHW Commissioning and Control System for Lodging Facilities, prepared by Energy and Environmental Analysis, Inc. (an ICF International Company), for Southern California Gas Company, Los Angeles, California, Version B, March 2008.

- Energy Efficiency Policy Manual, Version 2, California Public Utilities Commission, Sacramento, California, August 2003.

- Energy Efficiency Policy Manual, Version 3, California Public Utility Commission, Sacramento, California, March 2007.

- Principles of Heat Transfer, Frank Kreith, Intext Education Publishers, 1973.

- Revised / Updated EULS Based on Retention and Persistence Studies Results, Revised Report, by Lisa A. Skumatz, and John Gardner, Skumatz Economic Research Associates, Inc. (SERA, Inc), and Scott Dimetrosky and David Mattingly, Quantec, LLC, submitted to Marian Brown and Shahana Samiullah, Southern California Edison, July 8, 2005.

# List of Attachments

The following attachments support this workpaper (supplied as separate electronic files):

- Attachment #1 – Gas Savings from Programmable Setback

# Appendix A.	Common Types of Domestic Hot Water Systems

Domestic hot water (DHW) systems exist as commonplace in all aspects of our lives, whether at home or work.  While hot water availability has become ordinary, few users of hot water are aware that hot water creation is responsible for over 38% of all natural gas consumed in the United States.  When looking at an individual hot water environment, the consumption figures can become staggering.  Large DHW systems consume energy in two distinct ways:

- Hot water consumption

- Standby losses

###### A-1.	Hot Water Consumption

The first source of energy use is for water heated in relation to the domestic consumption of hot water for the showers and sinks in guest rooms at lodging facilities.  This water is heated in the water heater/boiler to a temperature that will satisfy peak demand hot water use.  The requirement for delivery temperature will vary dependant on the type of consumption.  Consumption for personal use requires temperatures to be between 100 and 110 degrees Fahrenheit (F); since higher temperatures may cause scalding.  To meet these needs, the actual temperature of the water will depend on the capacity of the water heating equipment.

Ideally, heating systems are sized to operate between 120 and 125 F.  This prevents excessive mineral buildup and condensation problems.  However, most are sized to operate at higher temperatures, typically 125 to 140 F.  If the system is undersized, it will require higher temperature settings in order to keep up with the demand.  As water temperature within the system is increased, the amount of cold water introduced at the faucet is also increased thus increasing the amount of hot water that is available for the overall system.

The amount of energy used to heat water for consumption is directly related to the amount of hot water used at the faucet, the efficiency at which the water is heated and delivered, and the temperature rise required to satisfy hot water needs (see Table 2).  The only effect that a control system has in relation to consumption is through the reduced energy requirement to heat the replenishing supply of cold water to a lesser degree for delivery.  However, this has a limited effect if a control system is properly programmed.  The required delivery temperatures will follow perceived demand with the highest temperatures occurring during highest demand periods; thus, during periods of high hot water, consumption the energy saved will be negligible.

Table 2.	Variables That Effect Energy Use Relating to Hot Water Consumption

| Changes in occupancy | Each individual person adds approximately 25 - 35 gallons of hot water consumption per day (approximately 1,000 gallons of hot water per month) or about 6 therms of gas consumption per month |
| --- | --- |
| Changes in Weather | In cooler weather people take hotter showers (approx 10 °F) equating to 1 therm increase per person per month or a 15% increase for cold days vs. hot days |
| The temperature of water supply to replenish the system | A 13 °F change (45 °F versus 58 °F) inlet water temperature = over 1 therm per month increase per person or 15% summer to winter increase |
| Desired temperature setting | 120 °F versus 130 °F increase in delivery temperature equals a 12% change in energy consumption per person |
| Hot water system sizing and efficiency | An undersized system will require hotter temperatures to supply demand. For every 10 °F temperature increase add approx. 12% increase in energy consumption to heat the water. |
| Changes in heating system operation or system degradation (i.e. crossover or pump problems) | Problems with system plumbing or equipment (especially crossover problems) create hot water consumption that is important in that it represents all wasted energy, for every gallon of water wasted while waiting for hot water, a new gallon of cold water is introduced into the system to be heated. The same effect happens when a re-circulating pump malfunctions or is disabled. A typical problem with a pump or crossover will account for 10 - 30 minutes of wasted water flow per day per person. At a minimum 2 gallons per minute that potentially represents an additional therm consumption of 6 or more therms per month per person |
| Other hot water consumption (GPM) | - Water leaks from various sources, such as leaking faucets or appliances - Crossover, which can be cold water leaking into the hot water system at mixing valves, or hot water leaking into the cold water system, whichever is at lower pressure - Underground leaks in the system plumbing - Impact on energy consumption can be major and difficult to quantify |

###### A-2.	Standby losses

The second source of energy use is energy consumed to compensate for standby losses.  Standby losses describe water that is continuously being reheated and staged for consumption (not water being consumed or lost).  In a single-family environment where a hot water system does not incorporate a re-circulating system, standby loss is limited to the heat losses at the water heater and plumbing to the faucets.  These heat losses have relatively little impact on the overall energy consumed when compared to a large distributed system.

In a multifamily, hospitality, or other large building where the distribution system incorporates a re-circulating pump to deliver readily available hot water, energy consumption for the systems standby losses may be greater than the energy consumption for the actual hot water use.  Different variables affect the energy consumed for standby losses than those discussed above for hot water consumption, including:

- Size and length of the distribution system

- Size and flow of the circulating pump (GPM)

- Type of medium the distribution system is exposed to (interior heated air, outside air with wind, underground)

- The overall temperature loss as water travels through the distribution system

- Efficiency of the water heater

- The effect weather may have relating to circulation loop losses

  - Ambient temperature as it relates to system losses

  - Ground water as it relates to system losses

  - Other influences

- Crossover, which can be cold water leaking into the hot water system at mixing valves, or hot water leaking into the cold water system, whichever is at lower pressure – This allows new cold water to be introduced into the hot water system in the circulation loop that, upon return to the hot water storage tank, will be heated and redistributed.

- Incorrectly installed or malfunctioning tempering valves that introduce a “built in” temperature loss into the system

  - Hot water is overheated for requirements other than direct consumption by people i.e. commercial kitchen/laundry then is tempered with cold water for other use and circulated back to the hot water source to be super heated once again

Unlike the variables that affect hot water consumption, the standby loss variables are relatively stable and can be easily determined.  Over the last several years, technologies have become available that make it very simple to isolate energy consumption relating to system losses verses energy used for hot water consumption.

The overall impact of energy consumed by standby losses can be significant.  The average boiler system in a large hotel can supply DHW for 40 to 500 hotel guest rooms, and has a complex distribution system several hundred feet in length.  It also incorporates one or more recirculation pumps.  A typical 100-unit property has flow rates in the distribution system of 20 to 25 gpm and a temperature loss of 10 to 15 F across the system, between the supply temperature and the return temperature.

The three most common types of boiler/heater configurations and their relative system efficiencies are described in the following.

###### A-3.	Modulating Boiler with No Storage Tank

A modulating boiler is an instantaneous or “on demand” boiler system without a storage tank (Figure 4).  This is the most inefficient system when installed on a recirculating hot water system.  This type of system is not applicable for a DHW setback control system unless a storage/mixing tank is installed.  This type of system utilizes modulating gas valves to regulate firing rate in relation to water temperature leaving the boiler.  As the water temperature decreases, the firing rate is increased to meet perceived demand.  These systems are proven to be inefficient on a circulation-type hot water system.

Figure 4	Modulating Boiler with No Storage Tank

Figure 5 shows an example of the delivery temperatures recorded for an instantaneous or on demand type hot water boiler system.  Since the temperature difference between low firing rate and high firing rate on a modulating gas valve is generally in the range of 9 to 20 °F (sometimes more), the highest water temperatures are generated during the periods of lowest hot water consumption.  Although it is counterintuitive, the greatest heat losses in the system occur during the lowest consumption periods.  The boiler delivery temperature tends to rise when the boilers operate at low firing rate to reheat recirculating water cooled in the loop.  The temperature rise is in relation to the operating range of the modulating gas valve, i.e., during high consumption, the boiler will operate at high firing rate at a temperature of 120 to 125 °F, while during low consumption, the firing rate will be at a minimum; however, the supply temperature will be 9 to 20 °F higher, implying a water temperature of 130 to 145 °F before the burner turns off.  The actual recorded hot water delivery temperature is highest at the times of lowest consumption.

Due to the high standby losses related to this type of system, energy consumed from the system is the greatest.  It is not uncommon to find systems of this type circulating hot water at 15 to 25 gpm with a 15 to 25 °F temperature loss or roughly half of the overall energy consumption used to reheat circulating water.  In this case, any reduction in delivery temperature, and thus standby loss, in the system during low periods of use will have a dramatic effect in overall energy consumption.  Typically systems of this type have an overall consumption per dwelling unit served that equals 25 to 50 or more therms per month, which is roughly double that of more efficient systems.

Average energy savings for this type of system are 15 to 20% due to the addition of a mixing tank and a thermostat but without a boiler control system, and 30 to 45% with a boiler control system.

Figure 5.	Daily Recorded Delivery Temperatures for an Instantaneous or On-Demand Type System

###### A-4.	Modulating Boiler with Tank and Thermostat

The addition of a storage/mixing tank to a modulating boiler system (as illustrated in Figure 6) increases the overall system efficiency for the following reasons:

- The re-circulating system is no longer utilized as a storage system to be used for mixing and blending of hot water coming from the boiler to eliminate hot/cold surges.

- The flow or re-circulation in the distribution loop can be reduced eliminating the need for a high volume pump on the distribution loop (the pump no longer needs to be sized in relation to boiler circulation needs).

- Low firing rate or idle temperature creep is eliminated by the newly installed tank thermostat, thus dramatically reducing off peak use, delivery temperatures and recirculation loop loses.

- The boiler will now work at a higher efficiency due to increased efficiencies when operating at high firing rate vs. low firing rate. (3-6%)

Figure 6.	Modulating Boiler with Storage Tank

Figure 7 shows the water temperatures for a modulating boiler system being controlled by a tank thermostat.  In this figure, Red (highest curve) indicates the maximum temperature achieved, Blue (lowest curve) is the minimum temperature achieved, and Green (middle curve) is the average temperature.

Modulating-input boiler systems with a tank thermostat operate much like a fixed-input boiler (i.e., an “on-off” controller).  When the thermostat calls for heat, the burner comes on with a high firing rate, and, as the thermostat approaches the upper temperature limit, the firing rate is reduced.  The tank thermostat may operate over a much smaller temperature range (2-7 °F) and may keep the tank and delivery temperatures regulated more closely during times of moderate and heavy hot water use.  Typical consumption per dwelling unit for this type of system is 15 to 25 therms per unit per month with standby losses accounting for 20 to 40% of the overall consumption dependant upon plumbing layout, e.g., exposed to conditioned air, underground lines.  Typical energy savings from adding a boiler control on this type of system is 15 to 25%.

Figure 7.	Charts for Modulating Boiler with Storage Tank

###### A-5.	Standard Commercial Water Heater with Integral Tank

A commercial type water heater with integral tank (Figure 8) is very common on medium sized systems of 8 – 30 units.  Some of the advantages are size and simplicity of installation and cost.  The disadvantages are lack of reparability, having a combined system does not allow for as much flexibility in a control strategy.  Typical energy consumption for these types of systems is 15 to 25 therms per month per dwelling unit controlled.  Energy savings potential using boiler controllers is between 13 and 23%.

Figure 8.	Standard Commercial Water Heater with Integral Tank

# Appendix B.	Gas Savings from Programmable Set-Back DHW Thermostat Controller

This appendix addresses the gas savings that can be expected as a result of applying the programmable setback feature of a domestic hot water (DHW) thermostat controller on DHW systems serving kitchen and laundry areas at lodging facilities.  Kitchen and laundry DHW use varies through each day in a consistent manner.  Like the automobile driver who presses the accelerator in anticipation of an upcoming hill, or the electric grid operator who brings additional generating capacity on-line in anticipation of the afternoon peak daily load, the supply temperature of a DHW system can be lowered at night to save energy and raised in the early morning in anticipation of the daytime load.  Peak DHW use in systems serving kitchen and laundry areas at lodging facilities generally occurs between 6 AM and 11 PM; while peak DHW use in systems serving laundry only generally occurs between 9 AM and 6 PM.  Between midnight and 5 AM, there is normally no hot water used in kitchen and laundry areas.

Applying a setback schedule reduces the heat loss from storage tank and boiler, the heat loss from piping, the heat used for ready hot water for consumption, the heat loss due to cross-over and, when the system has a piping loop, the heat loss in the piping loop.  To determine the setback schedule for each lodging facility, the DHW controller system must first monitor system parameters such as the following:

- Cumulative time in each half-hour period that the DHW controller requests each boiler to operate (i.e., the boiler control relay is closed)

- Cumulative time in each half-hour period that the boiler operates (i.e., boiler gas control valve is open)

- Supply temperature (temperature of hot water at the exit from the storage tank to the supply lines)

- Return temperature, if any (temperature of hot water returning from the piping loop)

Based on these data, the DHW controller setback schedule is determined empirically with man-in-loop.  The strategy is to lower the control temperature during periods of low DHW use and keep it highest during periods of high DHW use.  Since the kitchen and laundry areas rarely use hot water in the middle of the night, the control temperature is typically set to 105 °F during the nighttime.

This appendix is focused on gas savings from applying DHW controllers supplied and serviced by EDC Technologies on DHW systems serving kitchen and laundry areas at lodging facilities.  EDC collected kitchen and/or laundry temperature data at a dozen hotels in 2009.  As listed in Table 3, the data were collected during times when the DHW was controlled to constant temperature and during times when the controller programmable setback feature was used.  These hotels have controllers and boilers in the following configurations:

- One controller on one boiler connected to a storage tank serving the kitchen

- One controller on one boiler connected to a storage tank serving the kitchen and laundry together

- One controller on a two-stage boiler (with low fire and high fire) connected to a storage tank serving the kitchen

- One controller on two boilers operating simultaneously and in parallel to heat water in a storage tank serving the kitchen

- One controller on two boilers operating simultaneously and in parallel to heat water in a storage tank serving the kitchen and laundry together

- One controller on two boilers that are staged, i.e., the secondary boiler will only operate as needed, and they heat water in the same storage tank serving the kitchen and laundry together

- One controller on a boiler connected to a storage tank serving the kitchen, and a second controller on two boilers operating simultaneously and in parallel to heat water in a storage tank serving the laundry

Table 3.	Test Dates for Calculating Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback

| Controller | Area Served | Rooms per Controller | Constant Temperature Test |  | Setback Test |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  |  | Start Date | End Date | Start Date | End Date |
|  | Kitchen | 156 | 30-Mar-09 | 5-Apr-09 | 16-Mar-09 | 22-Mar-09 |
|  | Kitchen | 335 | 22-Apr-09 | 28-Apr-09 | 9-Apr-09 | 15-Apr-09 |
|  | Kitchen & Laundry | 210 | 21-Apr-09 | 27-Apr-09 | 9-Apr-09 | 16-Apr-09 |
|  | Kitchen | 258 | 17-Mar-09 | 23-Mar-09 | 9-Mar-09 | 15-Mar-09 |
|  | Laundry | 258 | 17-Mar-09 | 23-Mar-09 | 9-Mar-09 | 15-Mar-09 |
|  | Kitchen | 337 | 20-Apr-09 | 26-Apr-09 | 7-Apr-09 | 13-Apr-09 |
|  | Kitchen | 124 | 1-Apr-09 | 7-Apr-09 | 9-Apr-09 | 15-Apr-09 |
|  | Kitchen & Laundry | 161 | 17-Mar-09 | 24-Mar-09 | 8-Mar-09 | 15-Mar-09 |
|  | Kitchen | 309 | 21-Apr-09 | 27-Apr-09 | 9-Apr-09 | 15-Apr-09 |
|  | Kitchen & Laundry | 406 | 17-Mar-09 | 24-Mar-09 | 8-Mar-09 | 15-Mar-09 |
|  | Kitchen | 501 | 17-Mar-09 | 23-Mar-09 | 9-Mar-09 | 15-Mar-09 |
|  | Kitchen | 86 | 23-May-09 | 29-May-09 | 16-May-09 | 21-May-09 |

The test data consisted of boiler run-time data in the form of the number of seconds in each half-hour period when the boiler was operating.  The average results for 12 DHW systems are summarized in Table 4; the raw data and calculations are included as an electronic attachment.  The parameters listed in the table are the following:

- The average number of hotel guest rooms served per controller on DHW systems for kitchen and laundry areas

- The average boiler capacity per controller (MBtuh, thousands of BTU per hour)

- The gas used during the constant temperature test (the baseline), expressed in therms per year per controller (using 3600 seconds per hour, 48 half-hour periods per day, 365 days per year, and 100,000 Btu per therm)

- The gas used during the setback test (the measure), expressed in therms per year per controller

- The gas savings – the difference between the gas used during the constant temperature test and the gas used during the setback test, expressed in therms per year per controller

- The average gas savings between the constant temperature test and the setback test, expressed as a percentage of the gas used during the constant temperature test

Table 4.	Test Results for Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback

| Parameter | Average |
| --- | --- |
| Average numbers of guest rooms served per controller on DHW systems for kitchen and laundry areas | 262 |
| Average boiler capacity (MBtuh/controller) | 1,266 |
| Constant temperature gas use (therms/year/controller | 16,585 |
| Setback gas use (therms/year/controller) | 12,192 |
| Gas savings (therms/year/controller) | 4,393 |
| Average gas savings (% of constant temperature test) | 30.3% |

Table 5 provides additional statistical information on the test data for the boilers serving kitchen and laundry areas corresponding to each DHW system.  Due to variability in the design of the DHW systems at the various hotels, there is a wide range in the gas savings as a result of implementing programmable setback, with a correspondingly high standard deviation in the data.  However, the standard deviation of the average gas savings is only 909 therms per year per controller.

Table 5.	Statistical Analysis of Gas Savings by Changing from Controller Set at Constant Temperature to Programmable Setback

| Parameter | Average |
| --- | --- |
| Numbers of controllers tested | 12 |
| Average gas savings (therms/year/controller) | 4,393 |
| Minimum gas savings (therms/year/controller) | 1,053 |
| Maximum gas savings (therms/year/controller) | 11,378 |
| Standard error of gas savings (therms/year/controller) | 3,148 |
| Standard error of the average gas savings (therms/year/controller) | 909 |
| Total gas savings for all controllers tested (therms/year) | 52,716 |

Headquarters

ICF International

9300 Lee Highway

Fairfax, Virginia  22031

www.icfi.com

Washington State Office

12011 NE First Street

Suite 210

Bellevue, Washington  98005

T: (425) 688-0141

F: (425) 688-0180

Between Southern California Gas Company and EDC Technologies, Inc. and between San Diego Gas and Electric and EDC Technologies, Inc.

See DHW Commissioning and Control System for Lodging Facilities, prepared by Energy and Environmental Analysis, Inc. (an ICF International Company), for Southern California Gas Company, Los Angeles, California, Version B, March 2008.

Gas rate of 95 ¢/therm used for payback calculations.

Equipment Useful Life (EUL) is average continuous contract length or realization factor (91%) times 15 years.

NTG for “All other non-residential programs”

Cross-over is caused by leaks inside mixing valves which allow hot water to bleed into the cold water pipes or cold water to bleed into the hot water pipes (the flow direction depends upon the pressure difference at the valve).

It is protected by a username and password.

Energy Efficiency Policy Manual, Version 3, California Public Utility Commission, March 2007, which, in turn, references the Energy Efficiency Policy Manual, Version 2, California Public Utilities Commission, August 2003.  No data for DHW controllers was found in Revised / Updated EULS Based on Retention and Persistence Studies Results, Revised Report, by Lisa A. Skumatz, and John Gardner, Skumatz Economic Research Associates, Inc. (SERA, Inc), and Scott Dimetrosky and David Mattingly, Quantec, LLC, submitted to Marian Brown and Shahana Samiullah, Southern California Edison, July 8, 2005.

The 2007 ASHRAE Handbook on HVAC Applications, page 49.10, Table 3, recommends water temperatures of at least 150 °F for commercial spray-type dish washing which does not involve chemical sanitizing, but only 140 °F for commercial spray-type dish washing which involves chemical sanitizing.  They recommend temperatures up to 180 °F for commercial laundry, based on the fabric type.

As described in DHW Commissioning and Control System for Lodging Facilities, prepared by Energy and Environmental Analysis, Inc. (an ICF International Company), for Southern California Gas Company, Los Angeles, California, Version B, March 2008.

See Attachment #1 – Gas Savings from Programmable Setback

See Attachment #1 – Gas Savings from Programmable Setback

The standard deviation of the average is the standard error of the data divided by the square root of the number of data points using to calculate the average.