## Test Dates
Gas Savings from Controller Set at Constant Temperature to Programmable Setback
Controller | Area Served | Rooms per Controller | Constant Temperature Test |  | Setback Test
|  |  | Start Date | End Date | Start Date | End Date
| Kitchen | 156 | 2009-03-30 | 2009-04-05 | 2009-03-16 | 2009-03-22
| Kitchen | 335 | 2009-04-22 | 2009-04-28 | 2009-04-09 | 2009-04-15
| Kitchen & Laundry | 210 | 2009-04-21 | 2009-04-27 | 2009-04-09 | 2009-04-16
| Kitchen | 258 | 2009-03-17 | 2009-03-23 | 2009-03-09 | 2009-03-15
| Laundry | 258 | 2009-03-17 | 2009-03-23 | 2009-03-09 | 2009-03-15
| Kitchen | 337 | 2009-04-20 | 2009-04-26 | 2009-04-07 | 2009-04-13
| Kitchen | 124 | 2009-04-01 | 2009-04-07 | 2009-04-09 | 2009-04-15
| Kitchen & Laundry | 161 | 2009-03-17 | 2009-03-24 | 2009-03-08 | 2009-03-15
| Kitchen | 309 | 2009-04-21 | 2009-04-27 | 2009-04-09 | 2009-04-15
| Kitchen & Laundry | 406 | 2009-03-17 | 2009-03-24 | 2009-03-08 | 2009-03-15
| Kitchen | 501 | 2009-03-17 | 2009-03-23 | 2009-03-09 | 2009-03-15
| Kitchen | 86 | 2009-05-23 | 2009-05-29 | 2009-05-16 | 2009-05-21

## Per Controller
Gas Savings from Controller Set at Constant Temperature to Programmable Setback
Savings per Controller
Cost of equipment and installation ($/controller) | 1500
Cost of gas ($/therm) | 0.95
Controller | Courtyard Foothill Ranch Orange County | Crowne Plaza Hotel Irvine-Orange County Airport | Estancia La Jolla Hotel & Spa | Grand Del Mar |  | Hilton Concord | Hilton Garden Inn Arcadia | Hilton Garden Inn Milpitas | Hilton Ontario Airport | Hyatt Regency Newport Beach | Hyatt Regency Santa Clara | SpringHill Suites Arcadia
| Kitchen | Kitchen | K&L | Kitchen | Laundry | Kitchen | Kitchen | K&L | Kitchen | K&L | Kitchen | Kitchen
Numbers of room served | 156 | 335 | 210 | 258 | 258 | 337 | 124 | 161 | 309 | 406 | 501 | 86
Boiler capacity for unit #1 (MBtuh) | 275 | 900 | 1260 | 1200 | 1670 | 1200 | 399 | 399 | 750 |  | 1430 | 333
Boiler capacity for unit #2 (MBtuh) |  | 900 | 1260 |  | 1670 | 360 |  | 399 | 750 | 399
Avg Secs per 1/2 hr (Standard Ops) for unit #1 | 653 | 282 | 222 | 294 | 137 | 15 | 664 | 192 | 323 |  | 480 | 335
Avg Secs per 1/2 hr (Standard Ops) for unit #2 |  | 282 | 222 |  | 137 | 424 |  | 152 | 323 | 444
Avg Secs per 1/2 hr (Controlled Ops) for unit #1 | 169 | 245 | 192 | 148 | 67 | 2 | 345 | 147 | 270 |  | 441 | 270
Avg Secs per 1/2 hr (Controlled Ops) for unit #2 |  | 245 | 192 |  | 67 | 346 |  | 122 | 270 | 341
Boiler capacity (MBtuh) | 275 | 1800 | 2520 | 1200 | 3340 | 1200 | 399 | 798 | 1500 | 399 | 1430 | 333
Constant temperature gas use (therms/year) | 8739.3167 | 24703.2 | 27226.08 | 17169.6 | 22268.8933 | 8304.48 | 12893.552 | 6679.792 | 23579 | 8621.592 | 33404.8 | 5429.01
Setback gas use (therms/year) | 2261.7833 | 21462 | 23546.88 | 8643.2 | 10890.6267 | 6178.72 | 6699.21 | 5223.442 | 19710 | 6621.538 | 30690.66 | 4375.62
Gas savings (therms/year) | 6477.5333 | 3241.2 | 3679.2 | 8526.4 | 11378.2667 | 2125.76 | 6194.342 | 1456.35 | 3869 | 2000.054 | 2714.14 | 1053.39
Avg gas savings (% of baseline) | 74.12% | 13.12% | 13.51% | 49.66% | 51.09% | 25.6% | 48.04% | 21.8% | 16.41% | 23.2% | 8.125% | 19.4%
Number of controllers | 12
Parameter | Average | Minimum | Maximum | Std Dev | Std Dev of Mean | Total | Weighted Average
Numbers of room served per controller | 261.75 | 86 | 501 | 122.5532 | 0.95163 | 3141 | 0.18939
Boiler capacity (Mbtuh/controller) | 1266.1667 | 275 | 3340 | 945.0581 | 272.8148 | 15194 | 1266.1667
Constant temperature gas use (therms/year/controller) | 16584.943 | 5429.01 | 33404.8 | 9406.6782 | 2715.4741 | 199019.316 | 16584.943
Setback gas use (therms/year/controller) | 12191.9733 | 2261.7833 | 30690.66 | 9212.1492 | 2659.3184 | 146303.68 | 12191.9733 |  | Stdev/Avg
Gas savings (therms/year/controller) | 4392.9697 | 1053.39 | 11378.2667 | 3148.4749 | 908.8864 | 52715.636 | 4392.9697 |  | 71.67%
Avg gas savings (% of baseline) | 30.34% | 8.125% | 74.12% | 20.38% | 5.882% | 26.49% | 26.49%
Average cost savings ($/year/controller) | 4173.3212 | [5 empty] | 4173.3212
Average payback (years) | 0.35943 | [5 empty] | 0.35943
Note on G10: High fire
Note on G11: Low fire
Note on G16: High fire