Workpaper PGECOPRO105

Commercial Pool Heaters

Revision # 1

Pacific Gas & Electric Company

Customer Energy Solution

Commercial Pool Heaters

Measure Code H103

# At-A-Glance Summary

| Applicable Measure Codes: | H103 |
| --- | --- |
| Measure Description: | Installation of a commercial pool heater with higher efficiency than required by code. |
| Energy Impact Common Units: | Per 1,000 Btu/h heater input rating (kBtu/h) |
| Base Case Description: | The base case is installation of a pool heater meeting code-minimum thermal efficiency standards only. I.e. 82% thermal efficiency as required by Federal Code of Regulations effective April 16, 2013. |
| Base Case Energy Consumption: | Source: DOE Energy Smart Pools software. Varies by climate zone. |
| Measure Energy Consumption: | Source: DOE Energy Smart Pools software. Varies by climate zone. |
| Energy Savings (Base Case – Measure) | Source: DOE Energy Smart Pools software. Varies by climate zone. |
| Costs Common Units: | Per kBtu/h heater input rating |
| Base Case Equipment Cost ($/unit): | Source: PG&E survey of 41 models. $8.01 per kBtu/h input rating |
| Measure Equipment Cost ($/unit): | Source: PG&E survey of 41 models. $10.06 per kBtu/h input rating |
| Measure Incremental Cost ($/unit): | Source: PG&E survey. $2.05 per kBtu/h input rating |
| Effective Useful Life (years): | Source: DEER2011. 5 years |
| Measure Application Type: | Replace on Burnout (ROB) |
| Net-to-Gross Ratios: | Source: DEER2011, v4.01 0.60 |
| Important Comments: |  |

# At-A-Glance Measure List

Units = Per kBtu/h heater input rating

Note: For the complete list of Measures, refer to the attached calculation spreadsheet

# Work Paper Approvals

| Grant Brohard Manager, Technical Product Support | Date |
| --- | --- |
| Paola Benassi Manager, CES Core Products | Date |

# Document Revision History

| Revision # | Revision Date | Section-by-Section Description of Revisions | Author (Company) |
| --- | --- | --- | --- |
| Superseded |  | GAS WP Commercial Pool Heater.doc |  |
| Revision 0 | 04/01/2008 | Original workpaper Comm Pool Heaters PGECOPRO105 R0 | Peter Pollard (kW Engineering) |
| Revision 1 | 06/15/2012 | Update of original workpaper: Comm Pool Heaters PGECOPRO105 R1 - Expanded energy use analysis to include all Ca climate zones - Changed base case efficiency requirement from 78% to 82% thermal efficiency based on new Federal Code of Regulations requirement effective April 16, 2013 - Added comment regarding an evaluation made of an alternate software tool - Updated CEC Appliances Database data about current available units - Updated costs based on 2012 survey - Updated NTG Ratio - Changed applicability to pools only (not spas) | Peter Pollard (kW Engineering); Alina Zohrabian (PG&E) |

# Table of Contents

At-A-Glance Summary	i

At-A-Glance Measure List	ii

Work Paper Approvals	iii

Document Revision History	iv

Table of Contents	v

List of Tables	vi

Section 1. General Measure & Baseline Data	1

1.1 Product Measure Description & Background	1

1.3 Measure Application Type	2

1.4 Product Base Case and Measure Case Data	2

1.4.1 DEER Base Case and Measure Case Information	2

1.4.2 Codes & Standards Requirements Base Case and Measure Information	2

1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information	3

1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases	3

1.4.5 Time-of-Use Adjustment Factor	4

1.5 Summary of Inputs for Savings Calculations	4

Section 2. Calculation Methods	6

Measure Application Type	6

Measure Life Basis	6

First Baseline Period: Energy Savings Baseline	6

Second Baseline Period: Energy Savings Baseline	6

2.1 Electric Energy Savings Estimation Methodologies	6

2.2. Demand Reduction Estimation Methodologies	6

2.3. Gas Energy Savings Estimation Methodologies	6

Pool Heater Sizing	12

Determining Base and Measure Case Efficiencies	12

Gas Savings Results	13

Section 3. Load Shapes	16

3.1 Base Case Load Shapes	16

3.2 Measure Load Shapes	16

Section 4. Base Case & Measure Costs	16

4.1 Base Case(s) Costs	17

4.2 Measure Case Costs	17

4.3 Incremental & Full Measure Costs	17

Index	18

References	19

# List of Tables

Table 1 Measure Application Type	2

Table 2  Net-to-Gross Ratios	4

Table 3 Baseline by Measure Application Type	6

Table 4  Energy Smart Pools Software Inputs	8

Table 5  Energy Smart Pools Software Runs: Inputs, Results, Comments	10

Table 6  Energy Smart Pools Software Runs: Inputs, Results, Comments (cont’d)	11

Table 7  Results Summary and Normalization	14

Table 8  Results Summary and Normalization (cont’d)	15

# Section 1. General Measure & Baseline Data

## 1.1 Product Measure Description & Background

Catalog Description

To be eligible for a rebate the recipient must be a PG&E natural gas customer.  This rebate is available for swimming pool heating and unit must replace pre-existing pool heater. The commercial pool heater must be certified to meet the following requirements:  1) heater must be equal to or greater than 84% thermal efficiency, and 2) must have an “on/off” switch and have no pilot light.  Single Family accounts (residential homeowners) are not eligible for this product.

Program Restrictions and Guidelines

See Catalog Description above.

1.2 Product Technical Description

This measure is for the replacement of gas-fired pool water heaters with higher efficiency units. Current Title 20 Appliance Standards (1605.1g) require a minimum thermal efficiency of 78%, but a new federal standard of 82% will become effective April 16, 2013. Therefore the assumed base case efficiency for this measure is revised to code-minimum 82%. This measure is for heaters with a thermal efficiency of program-minimum 84% or higher.

This measure can apply to all heated pools installed in commercial facilities, such as schools, colleges, universities, YMCA/YWCA, public facilities, hotels/motels, health clubs, spas, homeowners association complexes, and other multi-family complexes.

Note that work done in PG&E’s Commercial Pool Pilot Program in 2006 and 2007 has shown that commercial pools divide into two segments: those smaller than 60,000 gallons and those larger than 60,000 gallons. Commercial pools smaller than 60,000 gallons typically use residential style pool equipment, featuring one or more heaters in the 300 to 400 kBtu/h size range. The applicability of this measure extends to all sizes to accommodate the energy savings opportunity associated with the significant number of smaller and larger heated commercial pools.

## 1.3 Measure Application Type

The DEER Measure Cost Data Users Guide found on www.deeresources.com under DEER2011 Database Format hyperlink, DEER2011 for 13-14, spreadsheet SPTdata_format-V0.97.xls, defines the terms as follows:

Table 1 Measure Application Type

Identifies the measure application type in the Measure Implementation table in DEER2011.

| Code | Description | Comment |
| --- | --- | --- |
| ER | Early retirement | measure applied while existing equipment still viable, or retrofit of existing equipment |
| ROB | Replace on Burnout | measure applied when existing equipment fails or maintenance requires replacement |
| NC | New Construction | measure applied during construction design phase as an alternative to a code-compliant standard design |

This measure is applicable to commercial installations only, and is offered as a Replace on Burnout (ROB) measure.

DEER2011 lists a 5 year Effective Useful Life (EUL) for commercial pool heaters.

## 1.4 Product Base Case and Measure Case Data

## 1.4.1 DEER Base Case and Measure Case Information

There is no DEER measure for commercial pool heaters.

## 1.4.2 Codes & Standards Requirements Base Case and Measure Information

The following codes currently apply to this measure. The pending new federal standard will set the baseline efficiency requirement.

Title 20: This measure is regulated under Title 20 of the California Energy Regulations (December 2010). Section 1605.1.g.1 requires:

(g) Pool Heaters, Portable Electric Spas Residential Pool Pump and Motor Combinations, and Replacement Pool Pump Motors.

(1) Energy Efficiency Standard for Gas-Fired Pool Heaters and Oil-Fired Pool Heaters. The thermal efficiency of gas-fired pool heaters and oil-fired pool heaters shall be not less than 78 percent.

The thermal efficiency values are determined by the required test method outlined in the standard, Section 1604(g). This section requires that test method ANSI Z21.56-1998 be followed for gas-fired pool heaters.

Title 24: This measure is similarly regulated under Title 24 of the California Energy Regulations (December 2008), which refers to the above Title 20 Appliance Standard, reprinted in Appendix B of the Title 24 Nonresidential Compliance Manual.

Federal Standards: The US Department of Energy has issued document 10 CFR Part 430 (Energy Conservation Program: Energy Conservation Standards for Residential Water Heaters, Direct Heating Equipment, and Pool Heaters) to amend part 430 of chapter II, subchapter D, of title 10 of the Code of Federal Regulations, to read as follows (Effective April 16, 2013):

PART 430—ENERGY CONSERVATION PROGRAM FOR CONSUMER

PRODUCTS

§430.32 Energy and water conservation standards and their effective dates.

(k) Pool heaters.

(2) Gas-fired pool heaters manufactured on or after April 16, 2013, shall have a thermal efficiency not less than 82%.

## 1.4.3 EM&V, Market Potential, and Other Studies – Base Case and Measure Case Information

There are no EM&V studies identified that address commercial pool heaters.

## 1.4.4 Assumptions and Calculations from other sources—Base and Measure Cases

Energy Savings Assumptions:

As noted in Section 1.4.2 above, the pending federal standard for pool heater efficiency is a minimum 82% thermal efficiency.

The savings estimates calculated for this measure assume this code-minimum efficiency of 82% as the base case efficiency for pool heaters to be replaced.

To determine the average pool heater efficiency in the measure case, the California Energy Commission (CEC) Appliance Database was used. Listings in the relevant database were narrowed to include only eligible pool heaters models for heating water using natural gas fuel with no pilot light and having an accessible on/off switch. These listings were then sorted by rated efficiency. Finally, a simple average of efficiency was calculated for all models with efficiency of at least 84%, the program-minimum efficiency specified for this measure, including very high efficiency condensing models. This average higher efficiency was 87.09%.

Hours of Operation:

Typical commercial pool hours of operation were assumed as 8am to 8pm, 7 day per week, 365 days per year.

Base Case Costs and Measure Case Costs:

See Section 4.

Effective Useful Life:

According to DEER 2011, version 4.01, the EUL for Commercial Pool Heaters is 5 years. (EUL_ID = WtrHt-GPoolHtr). The EUL of base case and most higher efficiency measure case units is expected to be similar.

Net-to-Gross Assumption:

The NTG ratio is from DEER2011. The most appropriate NTG value is shown in the table below.

Table 2  Net-to-Gross Ratios

| Program Approach | NTGR_ID, Description | NTG |
| --- | --- | --- |
| Commercial | Com-Default>2yrs, All other EEMs with no evaluated NTGR; existing EEM in programs with same delivery mechanism for more than 2 years | 0.60 |

## 1.4.5 Time-of-Use Adjustment Factor

We are required by CPUC decision 06-06-063 dated June 29, 2006 to apply time-of-use (TOU) adjustment factors on residential A/C and commercial A/C (packaged and split-system direct-expansion cooling) measures only. Since this is not an A/C measure, the TOU adjustment factor is 0.

## 1.5 Summary of Inputs for Savings Calculations

The following table provides references to sections that document the inputs for calculation:

| Input Variable | Variations | Base Case 1 Average Value | Base Case 2 Average Value | Measure Case Average Value | Reference Section |
| --- | --- | --- | --- | --- | --- |
| Electric Savings | n/a | n/a | n/a | n/a | 2.1 |
| Gas Savings (therms per kBtu/h capacity) | CZ | n/a | n/a | 2.2 | 2.3 |
| Hours of operation | None | 4360 | n/a | 4360 | 2.3 |
| Full Cost ($ per kBtu/h capacity) | None | $8.01 | n/a | $10.06 | 4.1, 4.2 |
| Incremental Cost ($ per kBtu/h capacity) | ROB | n/a | n/a | $2.05 | 4.3 |
| EUL /RUL | ROB | 5 | n/a | 5 | 1.4.4 |
| NTG | None | n/a | n/a | 0.60 | 1.4.4 |
| ISR | Applies -- Yes |  | n/a | 1 | n/a |
| TOU Factor | A/C projects only | 0 | n/a | 0 | 1.4.5 |

# Section 2. Calculation Methods

Table 3 Baseline by Measure Application Type

| ## Measure Application Type | ## Measure Life Basis | ## First Baseline Period: Energy Savings Baseline | ## Second Baseline Period: Energy Savings Baseline |
| --- | --- | --- | --- |
| ROB (replace-on-burnout) | EUL | Code Baseline | N/A |

Notes:

- For ROB measures, First Baseline is the baseline for the full EUL. There is no second baseline.

## 2.1 Electric Energy Savings Estimation Methodologies

There are no electric energy savings associated with this gas measure.

## 2.2. Demand Reduction Estimation Methodologies

There is no demand reduction associated with this gas measure.

## 2.3. Gas Energy Savings Estimation Methodologies

The U.S. Department of Energy (DOE) produced a software tool for estimating pool energy consumption as part of their Reduce Swimming Pool Energy Costs! Program (RSPEC!). This RSPEC! software tool (Energy Smart Pools Version 2.0a) was used to evaluate the typical energy savings for this measure. The software was run 35 times to estimate annual gas use for various conditions.

Note that Sandia National Laboratories recently evaluated various pool energy estimation software packages for a study of solar pool heating. They concluded that the RSPEC! tool produced the best load predictions as noted in the following excerpt:

Sizing the solar collector requires knowledge of how much heat is required to maintain a pool at the desired temperature. We used the RSPEC! software as our load estimating tool; we also compared RSPEC to these other tools and found considerable variation in the predicted load. We evaluated the various load predictions and came to the conclusion that the best load predictions are obtained using either the RSPEC! software tool or the RetScreen tool.

In addition, in early 2012, PG&E undertook a study to evaluate another newly-available online software tool for estimating pool energy consumption. The newer software is called Energy Experts, and was prepared by the Washington State University Extension Energy Program.  (http://energyexperts.org/CalculatorsTools/PoolEnergyUseCalculator.aspx). Testing of this software showed that it estimates far higher energy use than the DOE Energy Smart Pools tool, especially for outdoor pools. In order to evaluate which tool is more accurate, results were compared with four case study pools where metered data was available. While this sample was small, the results indicated very clearly that Energy Experts over-estimates energy use of outdoor pools - the Energy Experts usage estimates were on average 439% of the metered usage. Based on this study, as well as comparisons with another inhouse PG&E software tool and discussions with other engineers, it was concluded that the DOE Energy Smart Pools tool remains the best available for pool energy use analysis.

The Energy Smart Pools software has many inputs used to estimate energy use. Conditions with the highest sensitivity were selected for variation including indoor/outdoor, climate zone and types of covering. The following table lists the program inputs, assumptions made, plus notes regarding the sensitivity of energy use to each input.

Table 4  Energy Smart Pools Software Inputs

| Input | Assumption | Notes | Sensitivity |
| --- | --- | --- | --- |
| --General-- |  |  |  |
| Owner Type | Unknown | Averages all types |  |
| Indoor/Outdoor | Indoor 50%, Outdoor 50% | Assumed average | Very high (outdoor increases gas use by 100-150%) |
| Schedule | Year-round, 8am-8pm, 7 days per week | Assumed average |  |
| --Pool Data-- |  |  |  |
| Surface Area | 1,000 sq.ft. | Easily scalable |  |
| Pool Temperature | 80degF | Typ 78-82degF | Medium (higher pool temp increases gas use 5-6% per 1degF) |
| Activity Level | High | (High or Low) - Commercial pools assumed to be busy | Medium (Low activity lowers gas use by 11-15%) |
| --Outdoor Conditions-- |  | Apply to outdoor cases only |  |
| Location | Sacramento (Central Valley), San Francisco (North Coastal), San Diego/LA (South Coastal), Las Vegas NV (Desert proxy) | Limited selection in software | Medium (Sacramento lower gas use by 20% vs SF for outdoor pools) |
| Wind Speed % | 15% | Program default | Very High (higher wind coefficient increases gas use 19-24% per 10% wind) |
| Shading % | 30% | Program default | Medium (gas use higher 6-9% per 10% higher shading) |
| --Indoor Conditions-- |  | Apply to indoor cases only |  |
| Room Temperature | 72 degF |  | Medium (Higher room temp reduces gas use 3% per degF) |

| Input | Assumption | Notes | Sensitivity |
| --- | --- | --- | --- |
| Room Relative Humidity | 60% RH | Assumed average | High (lower room RH increases gas use 14% per 10%RH) |
| --Pool Cover Data-- |  |  |  |
| Cover | None | Assumed most common | Very High |
| Vinyl Cover, as below: |  |  | Use of vinyl cover reduces gas use 35-38% |
| -Cover R-Value | 0.2 | Program allows 0.1 – 0.5 |  |
| -Cover Coverage | 95% | Assumed average |  |
| Insulated Cover, as below: |  |  | Use of insulated cover reduces gas use 43-56% |
| -Cover R-Value | 2 | Program default |  |
| -Cover Coverage | 95% | Assumed average |  |
| Bubble/Solar Cover, as below: |  |  | Use of bubble/solar cover reduces gas use 40-42% |
| -Cover R-Value | 1.5 | Program default |  |
| -Cover Coverage | 95% | Assumed average |  |
| --Other Inputs-- |  |  |  |
| Vent heaters | Ignored |  |  |
| Pumps - all | Ignored |  |  |
| Solar Heating | None |  |  |

The following table presents inputs, results, and comments for 60 software runs.

Table 5  Energy Smart Pools Software Runs: Inputs, Results, Comments

Table 6  Energy Smart Pools Software Runs: Inputs, Results, Comments (cont’d)

### Pool Heater Sizing

Typical pool heater sizing is important for normalizing gas use savings by heater size (i.e. therms per kBtu/h heater rated input).

A survey of vendor literature indicates that commercial pool heaters are mainly sized based on:

- Pool surface area;

- Indoor vs outdoor installation;

- Temperature difference between pool temperature and worst-case ambient temperature (eg. average for coldest month of pool use);

- Required rate of temperature change (ie. for initial heat-up) may also be considered where relevant. This may be rated as required temperature change per 24 hours;

- Local conditions, including wind and sun exposure and typical humidity levels, can also be important.

Based on published vendor general recommendations, typical pool heater sizes are:

- 100 kBtu/h per 200-400 square feet (average 300) of surface area for outdoor pools; and

- 100 kBtu/h per 400-800 square feet (average 600) of surface area for small to large commercial indoor pools.

We used the above average values to convert gas savings from therms per square foot of pool area to therms per kBtu/h heater input rating. For example, for outdoor pools with an average 100 kBtu/h heater capacity per 300 square feet of pool area,

Gas Savings		=	Gas Savings	*	 300 sq.ft.

[therms/kBtu/h]		[therms/sq.ft.]	 100 kBtu/h.

### Determining Base and Measure Case Efficiencies

The gas energy savings was calculated based on the efficiency improvement from 82% in the base case to 87.09% in the measure case.

The base case efficiency is the code-minimum efficiency (82%) as discussed in section 1.4.2 above.

To determine the average pool heater efficiency in the measure case, the California Energy Commission (CEC) Appliance Database was used. Listings in the relevant database were narrowed to include only eligible pool heaters models for heating water using natural gas fuel with no pilot light and having an accessible on/off switch. These listings were then sorted by rated efficiency. Finally, a simple average of efficiency was calculated for all models with efficiency of at least 84%, the program-minimum efficiency specified for this measure, including very high efficiency condensing models. This average higher efficiency was 87.09%.

### Gas Savings Results

The table on the following page summaries results including normalization of the estimated savings to annual therms per kBtu/h heater input rating. Note that when normalized by heater size, savings are similar for indoor and outdoor pools.

Annual Gas Savings:

Energy Savings [therms/unit] = Annual Base Gas Usage – Annual Energy Efficient Gas Usage

The following Table 4 shows the results from the modeling runs along with the combined savings figures that comprise the program savings estimate.

Table 7  Results Summary and Normalization

Table 8  Results Summary and Normalization (cont’d)

# Section 3. Load Shapes

Load Shapes are an important part of the life-cycle cost analysis of any energy efficiency program portfolio.  The net benefits associated with a measure are based on the amount of energy saved and the avoided cost per unit of energy saved.  For electricity, the avoided cost varies hourly over an entire year.  Thus, the net benefits calculation for a measure requires both the total annual energy savings (kWh) of the measure and the distribution of that savings over the year.  The distribution of savings over the year is represented by the measure’s load shape.  The measure’s load shape indicates what fraction of annual energy savings occurs in each time period of the year.  An hourly load shape indicates what fraction of annual savings occurs for each hour of the year.  A Time-of-Use (TOU) load shape indicates what fraction occurs within five or six broad time-of-use periods, typically defined by a specific utility rate tariff.  Formally, a load shape is a set of fractions summing to unity, one fraction for each hour or for each TOU period.  Multiplying the measure load shape with the hourly avoided cost stream determines the average avoided cost per kWh for use in the life cycle cost analysis that determines a measure’s Total Resource Cost (TRC) benefit.

## 3.1 Base Case Load Shapes

Load shapes are not applicable to gas measures, however, because the price of gas is not dependent on time-of-use.

## 3.2 Measure Load Shapes

Load shapes are not applicable to gas measures, because the price of gas is not dependent on time-of-use.

# Section 4. Base Case & Measure Costs

An updated web search was undertaken in 2012 to obtain current market pricing for a wide range of pool heaters. The online CEC Appliances Database was used as a guide for models to be investigated. Only units using natural gas as fuel and without a pilot light were considered. A total of 189 models meeting these criteria are listed in the CEC database. This population of 189 pool heater models has an average input rating of 938 kBtu/h (median 400 kBtu/h), and an average thermal efficiency of 83.40% (median 82.00%). A total of 59 out of these 189 models has a thermal efficiency of 84% or higher, making them eligible for this measure.

Prices were obtained for 41 of these listed models. These 41 pool heater models were sorted based on eligibility for this measure (ie. thermal efficiency of 84+%, or lower, as reported on the CEC database.) In all cases, the lowest price obtained was used.

Please see the full pool heater model listing with prices in the appendix.

## 4.1 Base Case(s) Costs

The average price for pool heaters with thermal efficiency below 84% was found to be $8.01 per kBtu/h input rating.

## 4.2 Measure Case Costs

The average price for pool heaters with thermal efficiency of 84% and above was found to be $10.06 per kBtu/h input rating, or $2.05 higher than the base case.

## 4.3 Incremental & Full Measure Costs

Based on the above research and analysis, the incremental cost for a high-efficiency pool heater is estimated as $2.05 per kBtu/h input rating.

# Index

Base case	i, 1, 3, 4, 12, 17

CEC	3, 12, 16

Climate zone	7

DEER	2, 4

Efficiency	i, 1, 2, 3, 4, 12, 16, 17

EUL	2

Measure	1, 2, 3, 4, 6, 12, 16

PG&E	i, 1

Pool	i, 1, 2, 3, 6, 8, 12, 16, 17, 3, 12, 16

Savings	1, 3, 6, 12, 13, 16

Spa	i, 1, 2

Vendor	12, 12

# References

The DEER Measure Cost Data Users Guide found on www.deeresources.com under DEER2011 Database Format hyperlink, DEER2011 for 13-14, spreadsheet SPTdata_format-V0.97.xls.

DEER Database for Energy-Efficient Resources, Version 2011 4.01. EUL/RUL Values. Updated 10/10/2008. Web. Accessed 6/4/2012.

<http://deeresources.com/index.php?option=com_content&view=article&id=68&Itemid=60>.

U.S. Department of Energy, 10 CFR Part 430 [Docket Number: EE-2006-BT-STD-0129]

California Energy Commission Appliances Database, online at:

http://www.energy.ca.gov/appliances/database/

DEER2011_NTGR_2012-05-16.xls

Sandia National Laboratories, Large Scale Municipal and Commercial Solar Pools website – Engineering Tools and Heating Loads, http://energy.sandia.gov/engineeringtools.htm, last modified May 4, 2007.

See sample vendor literature with heater sizing methods from Hayward, Raypak, and Laars in the Appendix.

California Energy Commission Appliances Database, online at:

http://www.energy.ca.gov/appliances/database/

California Energy Commission Appliances Database, online at: http://www.energy.ca.gov/appliances/database/