# Residential New Construction
Measure Potential Analysis

Residential new construction is the appropriate marketplace for the promotion of new technologies, experimentation and improved energy efficiency measurement. This important market has been the spawning ground for numerous measures that have pushed the technical envelope and pioneered new energy efficiency approaches now considered mainstream in the retrofit market. With the changes to the California Building Energy Efficiency Standards (Standards), new credits will be available for the building industry to utilize in meeting or exceeding the Standards.

According to the California Energy Commission (CEC) and the 2005 Building Energy Efficiency Standards (Standards) there are additional energy efficiency opportunities in residential new construction design, especially in heating, cooling, insulation and water heating design. To help capture these savings, improve long-term energy efficiency and avoid lost opportunities, the following specific measures are proposed for the Southern California Gas and San Diego Gas & Electric 2006-2008 residential new construction energy efficiency program. To ascertain the energy savings, incremental costs and potential, an analysis of the following measures was undertaken.

- Maximum Cooling Capacity
This measure requires that air conditioners are sized according to the Alternative Compliance Method (ACM) methodology and the requirements for the combination of adequate air flow, verified ducting system and improved refrigerant charge or TXV are met and is field verified.

- Verified Ducting System (Tested Ducts)
This measure requires that duct systems are sealed and diagnostic testing is performed to verify that leakage is less than the specified criteria and is field verified.

- Insulation Quality Installation
This measure requires that insulation is properly installed based upon the Standards and is field verified.

- Tank Less Water Heaters
This measure requires that a tank less water heater is installed with a minimum recovery factor of 0.80.

- Improved Air Conditioning EER
This measure requires that the Energy Efficiency Rating (EER) of the air conditioning unit or heat pump is a minimum of 11.7.

The following details the incremental measure cost, base case prototypes, analysis methodology and results.

## Incremental Measure Costs

Table 1 presents the incremental cost for each measure included in this analysis. These costs are based upon research with vendors and manufacturers. These costs include equipment and verification. The Effective Useful Life is based upon the Database for Energy Efficient Resources (DEER). Calculations for savings will use a Net-To-Gross of 0.80.

Table 1:  Incremental Measure Costs

| MEASURE | EFFICIENCY | INCREMENTAL COST | EFFECTIVE USEFUL LIFE (YEARS) |
| --- | --- | --- | --- |
| Maximum Cooling Capacity, Single Family | N/A | $225/System | 15 |
| Maximum Cooling Capacity, Multifamily | N/A | $150/System | 15 |
| Verified Ducting System, Single Family | N/A | $125/System | 15 |
| Verified Ducting System, Multifamily | N/A | $100/System | 15 |
| Quality Insulation Installation, Single Family | N/A | $300/Dwelling Unit | 20 |
| Quality Insulation Installation, Multifamily | N/A | $100/Dwelling Unit | 20 |
| Tank Less Water Heater, Single Family | 0.80 Recovery Efficiency | $325/Unit | 15 |
| Tank Less Water Heater, Multifamily | 0.80 Recovery Efficiency | $325/Unit | 15 |
| Air Conditioner EER, Single Family | 13 SEER, 11.7 EER | $225/Unit | 15 |
| Air Conditioner EER, Multifamily | 13 SEER, 11.7 EER | $225/Unit | 15 |

## Base Case Prototypes

The two base case prototypes were selected that are representative of the single family dwellings and the multi-family buildings that have been submitted for review and inclusion in the current residential new construction energy efficiency program, California Energy Star® New Homes. The single-family dwelling is a two-story home of 3,524 square feet with average building characteristics and a two-zone HVAC system. Glazing was typical of building practices in Southern California. The multi-family building is a three-story structure with 12 dwelling units. The total structure is 9,206 square feet with building characteristics typical for Southern California. Tables 2 and 3 detail the specific building characteristics in the prototypes by CEC climate zone.

## Analysis Methodology

Each prototype was developed originally using the 2001 Energy Efficiency Standards. On October 1, 2005, the revised Standards will take effect. To determine the potential for energy savings each measure would generate it is necessary to model them using those standards. Utilizing the approved version of MICROPAS 7.0, each of the two prototypes was converted to this version. Tables 1 and 2 detail the compliance margin percentage that resulted from this conversion. None of the proposed measures were utilized for original compliance with the exception of verified ducting system in the multifamily prototype. This was removed during the modeling analysis.

To determine the energy savings each measure would produce throughout the Southern California area, the proposed design of the base prototype was compared to the proposed design of the prototype with only the specific measure incorporated in the analysis. This difference in source energy in kBtu/sq-ft/year was converted to kilowatts (kWh) and Therms. This was calculated for CEC climate zones 4-10 and 13-15, which represent the areas served by the utilities. The results for the Southern California climate zones are tabulated in Tables 4 and 5.

## Calculation Example

Therm Equation

(Source Energy Margin * Dwelling Square Footage) / 100 = Therms

KWh Equation

(Source Energy Margin * Dwelling Square Footage) / (3.4121415 * 3) = kWh

Example

Single Family, Tested Ducts, Climate Zone 4

Therm Energy Margin: 14.18 - 12.22 = 1.96 kBtu/sf/yr

Dwelling Square Footage = 3,524

Therefore: Therms Saved = (1.96 * 3,524 / 100) = 69.07/Dwelling

Since the single family example has two systems, the per system savings would be 34.54 Therms.

kWh Energy Margin: 4.13 – 3.88 = 0.25 kBtu/sf/yr

Dwelling Square Footage = 3,524

Therefore kWh Saved = (0.25 * 3,524) / (3.4121415 * 3) = 86.07

Since the single family example has two systems, the per system savings would be 43.03 kWh.

## Results

The energy savings produced by these measures vary significantly by climate zone. Those measures, connected to space cooling have the greatest impact in the inland areas. Water heating is for the most part climate zone neutral. Maximum cooling capacity and Verified Ducting Systems have both kWh and Therm savings with the Therm savings generated for both from the credit for Verified Ducting Systems. Quality Insulation being an envelope measure also has both Therm and kWh savings. Air conditioning EER and tank less water heating have only kWh or Therm savings respectively.

## Energy Conversion

Source Energy: All the energy used in delivering energy to a site, including power generation and transmission and distribution losses, to perform a specific function, such as space conditioning, lighting, or water heating. Approximately three watts (or 10.239 Btus) of energy is consumed to deliver one watt of usable electricity.

Source Energy Conversion (kBtu/sf/yr)

Gas Heating: (Source Energy Margin * SqFt)/100 = Therms

Electric Heating: (Source Energy Margin * SqFt)/(3.4121415*3) = kWh

Electric Cooling: (Source Energy Margin * SqFt)/(3.4121415*3) = kWh

Gas Water Heating: (Source Energy Margin * SqFt)/100 = Therms

Therm: One hundred thousand (100,000) British thermal units (1 therm = 100,000 Btu).

Watt Conversion: 1 watt hour (Wh) = 3.4121415 Btu.

| Table 2. Single Family Detached Base Case Prototype |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Climate Zone | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 13 | 14 | 15 |
| Dwelling Square Ft. | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 | 3,524 |
| Glazing % Area | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% | 17.7% |
| Glazing Area | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 | 622.5 |
| Type of Window | 2VL | 2VL | 2VL | 2VL | 2VL | 2VL | 2VL | 2VL | 2VL | 2VL |
| Glazing U-factor | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 |
| Glazing SHGC | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 |
| Wall Area | 3102 | 3102 | 3102 | 3102 | 3102 | 3102 | 3102 | 3102 | 3102 | 3102 |
| Wall | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |
| Roof Area | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 | 3524 |
| Roof | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |
| Radiant Barrier | No | No | No | No | No | No | No | No | No | No |
| TXV | No | No | No | No | No | No | No | No | No | No |
| Tested Ducts | No | No | No | No | No | No | No | No | No | No |
| Infiltration Testing | No | No | No | No | No | No | No | No | No | No |
| Duct Design | No | No | No | No | No | No | No | No | No | No |
| Duct R-value | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |
| SEER | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |
| AFUE | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 |
| Water Heater (Gal.) | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 | 75 |
| Water Heater (RE) | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 | 0.76 |
| Standard | 26.11 | 21.95 | 15.14 | 15.21 | 22.04 | 27.76 | 38.81 | 49.59 | 55.79 | 76.80 |
| Proposed | 28.63 | 24.47 | 15.94 | 16.47 | 25.74 | 33.45 | 48.19 | 69.62 | 83.11 | 118.18 |
| Margin | -2.52 | -2.52 | -0.80 | -1.26 | -3.70 | -5.69 | -9.38 | -20.03 | -27.32 | -41.38 |
| Compliance Margin | -9.65% | -11.48% | -5.28% | -8.28% | -16.79% | -20.50% | -24.17% | -40.39% | -48.97% | -53.88% |

| Table 3. Multi-Family Low Rise Building Base Case Prototype |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Climate Zone | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 13 | 14 | 15 |
| Building Square Ft. | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 | 9,206 |
| Glazing % Area | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% | 12.7% |
| Glazing Area | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 | 1171.3 |
| Type of Window | V2L | V2L | V2L | V2L | V2L | V2L | V2L | V2L | V2L | V2L |
| Glazing U-factor | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 |
| Glazing SHGC | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 | 0.40 |
| Wall Area | 9710 | 9710 | 9710 | 9710 | 9710 | 9710 | 9710 | 9710 | 9710 | 9710 |
| Wall | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |
| Roof Area | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 | 5012 |
| Roof | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 | 30 |
| Radiant Barrier | No | No | No | No | No | No | No | No | No | No |
| TXV | No | No | No | No | No | No | No | No | No | No |
| Tested Ducts | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes | Yes |
| Infiltration Testing | No | No | No | No | No | No | No | No | No | No |
| Duct Design | No | No | No | No | No | No | No | No | No | No |
| Duct R-value | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 | 4.2 |
| SEER | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 | 13 |
| AFUE | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 | 0.80 |
| Water Heater (Gal.) | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 | 50 |
| Water Heater (EF) | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 | 0.62 |
| Standard | 41.20 | 36.86 | 31.79 | 31.88 | 40.62 | 47.55 | 60.27 | 66.99 | 76.27 | 98.95 |
| Proposed | 37.52 | 32.34 | 26.78 | 28.34 | 38.15 | 45.94 | 60.75 | 76.28 | 90.80 | 124.04 |
| Margin | 3.68 | 4.52 | 5.01 | 3.54 | 2.47 | 1.61 | -0.48 | -9.29 | -14.53 | -25.09 |
| Compliance Margin | 8.93% | 12.26% | 15.76% | 11.10% | 6.08% | 3.39% | -0.80% | -13.87% | -19.05% | -25.36% |

These two base case prototypes where selected from a database of more than 1,500 different architectural plans submitted for review and inclusion in the California Energy Star® New Homes Program. Each input file used for analysis received a detail plan review to insure it accurately reflected the plans.