## Boiler WH
MULTI FAMILY RCP PROGRAM
Analysis of Program Elements
Climate Zone | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback | Climate Zone | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback
Central Boilers: DHW Heating Only | [15 empty] | Central Storage Water Heaters: DHW Heating Only
| Small Apartments |  |  |  |  | Mid Size Apartments |  |  |  |  | Large Apartments | [5 empty] | Small Apartments
1 thru 16 | 4000 | 428.5714 | 214.2857 | 1000 | 39.6667 | 7000 | 750 | 375 | 1500 | 22.9333 | 11250 | 1205.3571 | 602.6786 | 2000 | 17.2563 | 1 thru 16 | 2400 | 257.1429 | 128.5714 | 550 | 26.8333
[5 empty] | 8500 |  |  |  |  | 8600 | [10 empty] | 3450
Central Boilers: DHW and Space Heating | [15 empty] | Central Storage Water Heaters: DHW and Space Heating
| Small Apartments |  |  |  |  | Mid Size Apartments |  |  |  |  | Large Apartments | [5 empty] | Small Apartments
1 | 11573.3333 | 1240 | 620 | 1000 | 13.7097 | 20253.3333 | 2170 | 1085 | 1500 | 7.9263 | 32550 | 3487.5 | 1743.75 | 2000 | 5.9642 | 1 | 6944 | 744 | 372 | 550 | 9.2742
2 | 8800 | 942.8571 | 471.4286 | 1000 | 18.0303 | 15400 | 1650 | 825 | 1500 | 10.4242 | 24750 | 2651.7857 | 1325.8929 | 2000 | 7.8438 | 2 | 5280 | 565.7143 | 282.8571 | 550 | 12.197
3 | 9013.3333 | 965.7143 | 482.8571 | 1000 | 17.6036 | 15773.3333 | 1690 | 845 | 1500 | 10.1775 | 25350 | 2716.0714 | 1358.0357 | 2000 | 7.6581 | 3 | 5408 | 579.4286 | 289.7143 | 550 | 11.9083
4 | 9226.6667 | 988.5714 | 494.2857 | 1000 | 17.1965 | 16146.6667 | 1730 | 865 | 1500 | 9.9422 | 25950 | 2780.3571 | 1390.1786 | 2000 | 7.4811 | 4 | 5536 | 593.1429 | 296.5714 | 550 | 11.6329
5 | 9440 | 1011.4286 | 505.7143 | 1000 | 16.8079 | 16520 | 1770 | 885 | 1500 | 9.7175 | 22050 | 2362.5 | 1181.25 | 2000 | 8.8042 | 5 | 5664 | 606.8571 | 303.4286 | 550 | 11.3701
6 | 7840 | 840 | 420 | 1000 | 20.2381 | 13720 | 1470 | 735 | 1500 | 11.7007 | 22050 | 2362.5 | 1181.25 | 2000 | 8.8042 | 6 | 4704 | 504 | 252 | 550 | 13.6905
7 | 6880 | 737.1429 | 368.5714 | 1000 | 23.062 | 12040 | 1290 | 645 | 1500 | 13.3333 | 19350 | 2073.2143 | 1036.6071 | 2000 | 10.0327 | 7 | 4128 | 442.2857 | 221.1429 | 550 | 15.6008
8 | 6986.6667 | 748.5714 | 374.2857 | 1000 | 22.7099 | 12226.6667 | 1310 | 655 | 1500 | 13.1298 | 19650 | 2105.3571 | 1052.6786 | 2000 | 9.8796 | 8 | 4192 | 449.1429 | 224.5714 | 550 | 15.3626
9 | 6880 | 737.1429 | 368.5714 | 1000 | 23.062 | 12040 | 1290 | 645 | 1500 | 13.3333 | 19350 | 2073.2143 | 1036.6071 | 2000 | 10.0327 | 9 | 4128 | 442.2857 | 221.1429 | 550 | 15.6008
10 | 7626.6667 | 817.1429 | 408.5714 | 1000 | 20.8042 | 13346.6667 | 1430 | 715 | 1500 | 12.028 | 21450 | 2298.2143 | 1149.1071 | 2000 | 9.0505 | 10 | 4576 | 490.2857 | 245.1429 | 550 | 14.0734
11 | 9546.6667 | 1022.8571 | 511.4286 | 1000 | 16.6201 | 16706.6667 | 1790 | 895 | 1500 | 9.6089 | 26850 | 2876.7857 | 1438.3929 | 2000 | 7.2303 | 11 | 5728 | 613.7143 | 306.8571 | 550 | 11.243
12 | 9226.6667 | 988.5714 | 494.2857 | 1000 | 17.1965 | 16146.6667 | 1730 | 865 | 1500 | 9.9422 | 25950 | 2780.3571 | 1390.1786 | 2000 | 7.4811 | 12 | 5536 | 593.1429 | 296.5714 | 550 | 11.6329
13 | 8480 | 908.5714 | 454.2857 | 1000 | 18.7107 | 14840 | 1590 | 795 | 1500 | 10.8176 | 23850 | 2555.3571 | 1277.6786 | 2000 | 8.1398 | 13 | 5088 | 545.1429 | 272.5714 | 550 | 12.6572
14 | 9333.3333 | 1000 | 500 | 1000 | 17 | 16333.3333 | 1750 | 875 | 1500 | 9.8286 | 26250 | 2812.5 | 1406.25 | 2000 | 7.3956 | 14 | 5600 | 600 | 300 | 550 | 11.5
15 | 6560 | 702.8571 | 351.4286 | 1000 | 24.187 | 11480 | 1230 | 615 | 1500 | 13.9837 | 18450 | 1976.7857 | 988.3929 | 2000 | 10.5221 | 15 | 3936 | 421.7143 | 210.8571 | 550 | 16.3618
16 | 13706.6667 | 1468.5714 | 734.2857 | 1000 | 11.5759 | 23986.6667 | 2570 | 1285 | 1500 | 6.6926 | 38550 | 4130.3571 | 2065.1786 | 2000 | 5.0359 | 16 | 8224 | 881.1429 | 440.5714 | 550 | 7.8307
Assumptions: | [9 empty] | 8600 | [5 empty] | Assumptions:
| Gas Rate $/Therm |  |  | 0.5 | [12 empty] | Gas Rate $/Therm |  |  | 0.5
| Existing Boiler efficiency |  |  | 75% | [12 empty] | Existing Boiler efficiency |  |  | 75%
| Proposed Boiler efficiency |  |  | 84% | [12 empty] | Proposed Boiler efficiency |  |  | 84%
| Incentive per MBTU |  |  | 2 | [12 empty] | Incentive per MBTU |  |  | 2
| Apt Size | Range of Units | Av Units | Boiler Size MBTU | Equip Cost | [11 empty] | Apt Size | Av Units | Water Htr Size MBTU | Equip Cost
| Small | 20 - 30 | 25 | 500 | 9500 | [11 empty] | Small | 15 | 275 | 4000
| Mid Size | 30 - 40 | 35 | 750 | 10100
| Large | 40 - 50 | 45 | 1000 | 12400

## WH Controller
MULTI FAMILY RCP PROGRAM
Analysis of Program Elements
Central Water Heater Controllers: DHW Heating Only
Climate Zone | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback | Demand Therm | Savings Therm | Savings Cost | Incentive per Unit | Simple Payback
| Mid Size Apartments |  |  |  |  | Large Apartments
1 thru 16 | 6000 | 900 | 450 | 2700 | 1.7778 | 12500 | 1875 | 937.5 | 2812.5 | 0.73333
Central Water Heater Controllers: DHW and Space Heating
| Mid Size Apartments |  |  |  |  | Large Apartments
1 | 17360 | 3472 | 1736 | 3124.8 | 0.21613 | 36166.6667 | 7233.3333 | 3616.6667 | 3616.6667 | -0.032258
2 | 13200 | 2640 | 1320 | 2376 | 0.85152 | 27500 | 5500 | 2750 | 2750 | 0.27273
3 | 13520 | 2704 | 1352 | 2433.6 | 0.78876 | 28166.6667 | 5633.3333 | 2816.6667 | 2816.6667 | 0.2426
4 | 13840 | 2768 | 1384 | 2491.2 | 0.7289 | 28833.3333 | 5766.6667 | 2883.3333 | 2883.3333 | 0.21387
5 | 14160 | 2832 | 1416 | 2548.8 | 0.67175 | 29500 | 5900 | 2950 | 2950 | 0.18644
6 | 11760 | 2352 | 1176 | 2116.8 | 1.1762 | 24500 | 4900 | 2450 | 2450 | 0.42857
7 | 10320 | 2064 | 1032 | 1857.6 | 1.5915 | 21500 | 4300 | 2150 | 2150 | 0.62791
8 | 10480 | 2096 | 1048 | 1886.4 | 1.5397 | 21833.3333 | 4366.6667 | 2183.3333 | 2183.3333 | 0.60305
9 | 10320 | 2064 | 1032 | 1857.6 | 1.5915 | 21500 | 4300 | 2150 | 2150 | 0.62791
10 | 11440 | 2288 | 1144 | 2059.2 | 1.2594 | 23833.3333 | 4766.6667 | 2383.3333 | 2383.3333 | 0.46853
11 | 14320 | 2864 | 1432 | 2577.6 | 0.64413 | 29833.3333 | 5966.6667 | 2983.3333 | 2983.3333 | 0.17318
12 | 13840 | 2768 | 1384 | 2491.2 | 0.7289 | 28833.3333 | 5766.6667 | 2883.3333 | 2883.3333 | 0.21387
13 | 12720 | 2544 | 1272 | 2289.6 | 0.95157 | 26500 | 5300 | 2650 | 2650 | 0.32075
14 | 14000 | 2800 | 1400 | 2520 | 0.7 | 29166.6667 | 5833.3333 | 2916.6667 | 2916.6667 | 0.2
15 | 9840 | 1968 | 984 | 1771.2 | 1.7569 | 20500 | 4100 | 2050 | 2050 | 0.70732
16 | 20560 | 4112 | 2056 | 3700.8 | -0.097665 | 42833.3333 | 8566.6667 | 4283.3333 | 4283.3333 | -0.18288
Assumptions:
| Gas Rate $/Therm | [6 empty] | 0.5
| DHW Heating Percent Savings | [6 empty] | 15%
| Combined DHW and Hydronic Space Heating Percent Savings | [6 empty] | 20%
| Apt Size | Range of Units | Av Units | Controller Cost | DHW only Incentive $/therm | DHW+Sp Htg Incentive $/therm |  | Savings per Unit | Savings per unit x Av. Units | Average Units per Controller
| Mid Size | 20 - 40 | 30 | 3500 | 3 | 0.9 |  | 30 | 540 | 18
| Large | 40 - 60 | 50 | 3500 | 1.5 | 0.5 |  | 37.5 | 1500 | 40
| Very Large |  | > 60 | 3500 | No Analysis Done
Convert to be consistent with 2004 program

## Wall Furnace
MULTI FAMILY RCP PROGRAM
Analysis of Program Elements
WALL FURNACES
Assumptions:
Existing wall furnaces are 25-30 years old.
Can design an early replacement program to replace them 7-8 years earlier
Exist wall furnace effcy = 50%, new furnace = 70%
Gas Rate | 0.5 | $/th
Furnace Cost |  | 700
Type of Home |  | Climate | Annual Fuel Consumed |  | Savings | Cost | Furnace
|  | Zone | 50% Effcy | 70%Effcy | Th/Yr | Savings($) | Cost ($)
MF Pre-T-24 |  | 1 | 703.9519 | 507.8491 | 196.1028 | 98.0514 | 700
MF Pre-T-24 |  | 2 | 623.0238 | 449.4692 | 173.5546 | 86.7773 | 700
MF Pre-T-24 |  | 3 | 389.8168 | 281.228 | 108.5888 | 54.2944 | 700
MF Pre-T-24 |  | 4 | 411.3828 | 296.7662 | 114.6165 | 57.3083 | 700
MF Pre-T-24 |  | 5 | 371.2424 | 267.833 | 103.4094 | 51.7047 | 700
MF Pre-T-24 |  | 6 | 172.7062 | 124.5958 | 48.1104 | 24.0552 | 700
MF Pre-T-24 |  | 7 | 141.92 | 102.3825 | 39.5376 | 19.7688 | 700
MF Pre-T-24 |  | 8 | 169.0449 | 121.9838 | 47.0611 | 23.5305 | 700
MF Pre-T-24 |  | 9 | 191.5262 | 138.1694 | 53.3567 | 26.6784 | 700
MF Pre-T-24 |  | 10 | 259.2379 | 186.9942 | 72.2437 | 36.1219 | 700
MF Pre-T-24 |  | 11 | 625.993 | 451.6124 | 174.3806 | 87.1903 | 700
MF Pre-T-24 |  | 12 | 555.2674 | 400.5551 | 154.7122 | 77.3561 | 700
MF Pre-T-24 |  | 13 | 457.3723 | 329.9412 | 127.4311 | 63.7156 | 700
MF Pre-T-24 |  | 14 | 640.5935 | 462.1498 | 178.4437 | 89.2219 | 700
MF Pre-T-24 |  | 15 | 134.0393 | 96.6896 | 37.3497 | 18.6749 | 700
MF Pre-T-24 |  | 16 | 1508.2547 | 1088.0758 | 420.1788 | 210.0894 | 700
Proposed incentive level = |  |  | 200-300/unit

## Summary Savings
MULTI FAMILY RCP PROGRAM
BASELINE ENERGY USE CALCULATIONS BY CLIMATE ZONES
Climate Zone | DHW |  |  | Space Heating |  |  | Mowris | DHW + Space Heating |  |  | Wall Furnace
| Small | Medium | Large | Small | Medium | Large | SpHtgSavg | Small | Medium | Large | 50% | 70% | Savings
Climate Zone 1 | 160 | 200 | 250 | 302.9333 | 378.6667 | 473.3333 | 3195 | 462.9333 | 578.6667 | 723.3333 | 703.9519 | 507.8491 | 196.1028 | 454.4 | 250
Climate Zone 2 | 160 | 200 | 250 | 192 | 240 | 300 | 2025 | 352 | 440 | 550 | 623.0238 | 449.4692 | 173.5546 | 288
Climate Zone 3 | 160 | 200 | 250 | 200.5333 | 250.6667 | 313.3333 | 2115 | 360.5333 | 450.6667 | 563.3333 | 389.8168 | 281.228 | 108.5888 | 300.8
Climate Zone 4 | 160 | 200 | 250 | 209.0667 | 261.3333 | 326.6667 | 2205 | 369.0667 | 461.3333 | 576.6667 | 411.3828 | 296.7662 | 114.6165 | 313.6
Climate Zone 5 | 160 | 200 | 250 | 217.6 | 272 | 340 | 2295 | 377.6 | 472 | 590 | 371.2424 | 267.833 | 103.4094 | 326.4
Climate Zone 6 | 160 | 200 | 250 | 153.6 | 192 | 240 | 1620 | 313.6 | 392 | 490 | 172.7062 | 124.5958 | 48.1104 | 230.4
Climate Zone 7 | 160 | 200 | 250 | 115.2 | 144 | 180 | 1215 | 275.2 | 344 | 430 | 141.92 | 102.3825 | 39.5376 | 172.8
Climate Zone 8 | 160 | 200 | 250 | 119.4667 | 149.3333 | 186.6667 | 1260 | 279.4667 | 349.3333 | 436.6667 | 169.0449 | 121.9838 | 47.0611 | 179.2
Climate Zone 9 | 160 | 200 | 250 | 115.2 | 144 | 180 | 1215 | 275.2 | 344 | 430 | 191.5262 | 138.1694 | 53.3567 | 172.8
Climate Zone 10 | 160 | 200 | 250 | 145.0667 | 181.3333 | 226.6667 | 1530 | 305.0667 | 381.3333 | 476.6667 | 259.2379 | 186.9942 | 72.2437 | 217.6
Climate Zone 11 | 160 | 200 | 250 | 221.8667 | 277.3333 | 346.6667 | 2340 | 381.8667 | 477.3333 | 596.6667 | 625.993 | 451.6124 | 174.3806 | 332.8
Climate Zone 12 | 160 | 200 | 250 | 209.0667 | 261.3333 | 326.6667 | 2205 | 369.0667 | 461.3333 | 576.6667 | 555.2674 | 400.5551 | 154.7122 | 313.6
Climate Zone 13 | 160 | 200 | 250 | 179.2 | 224 | 280 | 1890 | 339.2 | 424 | 530 | 457.3723 | 329.9412 | 127.4311 | 268.8
Climate Zone 14 | 160 | 200 | 250 | 213.3333 | 266.6667 | 333.3333 | 2250 | 373.3333 | 466.6667 | 583.3333 | 640.5935 | 462.1498 | 178.4437 | 320
Climate Zone 15 | 160 | 200 | 250 | 102.4 | 128 | 160 | 1080 | 262.4 | 328 | 410 | 134.0393 | 96.6896 | 37.3497 | 153.6
Climate Zone 16 | 160 | 200 | 250 | 388.2667 | 485.3333 | 606.6667 | 4095 | 548.2667 | 685.3333 | 856.6667 | 1508.2547 | 1088.0758 | 420.1788 | 582.4
Assumptions:
Assumes that due to reduction in piping distances, per unit consumption in medium and
small apartments will be 20% lower successively
Small Apartment Complex |  |  | 20% | reduction from Medium
Medium Apartment Complex |  |  | 20% | reduction from Large
Large Apartment Unit Complex |  |  | Consumptions based on Mowris study.
Mowris study assumed same DHW consumption per unit over all Climate Zones.
Mowris study calculated space heating savings by climate zones from computer simulation
Assumed 15% savings from space heating energy use.
This is used to back calculate space heating energy use.
Mowris study was based on a 45 unit complex.
Wall furnace savings based on energy consumption difference between a 50% AFUE old
furnace and a 70% AFUE new furnace