## L2L Tool
Gas Savings Calculation for Like-to-Like Replacement of
Equipment Name
Method to Characterize Equipment Performance (select one)
Equipment performance is characterized by efficiency
Equipment performance is characterized by gas consumption per unit of production
Parameter |  |  | Scenario
|  |  | Baseline | Efficiency Measure | Notes
Equipment Load and Annual Use Inputs
1. Connected load (MBtuh) |  |  | 50000 |  | Enter result from Report tab of Load Balance Program
2. Operating time (hrs/yr) |  |  | 7749 |  | Enter result from Report tab of Load Balance Program
3. Load factor |  |  | 40% |  | Enter result from Report tab of Load Balance Program
4. Equivalent full load hours (hrs/yr) |  |  | 3099.6 |  | EFLH = OperatingTime * LoadFactor
5. Annual gas use (therms/yr) |  |  | 1549800 |  | BaselineGasUse = ConnectedLoad * EFLH / 100
Gas Savings based on Equipment Efficiency
6. Equipment efficiency |  |  | 78 | 84 | Retreive data from equipment spec sheet or manufacturer
7. Data Source |  | Enter text here |  |  | Provide data source(s) for the above efficiency values
8. Annual gas use (therms/yr) |  |  | 1549800 | 1439100 | MeasureGasUse = BaselineGasUse * BaselineEfficieny / MeasureEfficiency
9. Gas savings (%) |  |  | 7.143% |  | GasSavings% = 1 - BaselineEfficieny / MeasureEfficiency
10. Annual gas savings (therms/year) |  |  | 110700 |  | GasSavings = BaselineGasUse * (1 - BaselineEfficieny / MeasureEfficiency)
Cost Savings based on Equipment Efficiency
11. Gas rate ($/therm) |  |  | 0.95 |  | Customer gas rate
12. Annual cost savings ($/year) |  |  | 105165 |  | CostSavings = GasSavings * GasRate
Gas Savings based on Gas Consumption per Unit of Production
13. Gas use per unit of production |  | Enter units (Btu/lb, Btu/gal, etc.) | 1200 | 1100 | Retreive data from equipment spec sheet or manufacturer
14. Data source |  | Enter text here |  |  | Provide data source(s) for the above values for gas use per unit of production
15. Annual gas use (therms/yr) |  |  | 1549800 | 1420650 | MeasureGasUse = BaselineGasUse * MeasureGasUsePerUnit / BaselineGasUsePerUnit
16. Gas savings (%) |  |  | 8.333% |  | GasSavings% = 1 - MeasureGasUsePerUnit / BaselineGasUsePerUnit
17. Annual gas savings (therms/year) |  |  | 129150 |  | GasSavings = BaselineGasUse * (1 - MeasureGasUsePerUnit / BaselineGasUsePerUnit)
Cost Savings based on Gas Consumption per Unit of Production
18. Gas rate ($/therm) |  |  | 0.95 |  | Customer gas rate
19. Annual cost savings ($/year) |  |  | 122692.5 |  | CostSavings = GasSavings * GasRate
Disclaimer The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Note on B5: Input: Choose this option if the efficiency is the industry convention to characterize the performance of the gas equipment.
Note on B6: Input: Choose this option if the gas consumption per unit of production is the industry convention to characterize the performance of the gas equipment.
Note on C2: Input: Enter name of equipment being replaced, e.g., Hot Water Boiler
Note on C25: Input: Enter units: Btu/lb, kJ/L, Btu/gal, Btu/piece, etc.
Note on D10: Input: Connected load is Input rating or Firing rate
Note on D11: Input: Annual operating time includes scheduled time the equipment is turned on but not using gas
Note on D12: Input: Load factor is EFLH as a percent of operating time
Note on D16: Input: Baseline equipment efficiency per manufacturer's specification
Note on D25: Input: Baseline equipment specification for gas comsumption per unit of production
Note on E16: Input: Measure equipment specification: match type and units as baseline equipment specification
Note on E25: Input: Measure equipment specification: match type and units as baseline equipment specification

## Instructions
Instructions for
Like-to-Like Equipment Replacement
Enter name of equipment being replaced, e.g., Hot Water Boiler
To keep a record of the equipment being replaced.
Select Method to Characterize Equipment Performance
Selecting the appropriate button hides the inputs and results for the other method
Choose the first option if efficiency is the industry convention to characterize the performance of the gas equipment.
Choose the second option if the gas consumption per unit of production is the industry convention to characterize the performance of the gas equipment. For example, Btu of gas per unit of product (lbs, gallons, pieces).
Equipment Load and Annual Use Inputs
Inputs (cells with blue font)
Use Load Balance Tool to determine these inputs
Customer supplied information that varies from the Load Balance Tool requires approval
1. Connected load (MBtuh)
Equipment input rating provided by the customer
May be available from the MAS database
2. Equipment operating time (hours/year)
3. Equipment load factor (equivalent full load hrs/year as a percent of operating time)
Intermediate Results
4. Equivalent full load hours (hours/year)
EFLH = OperatingTime * LoadFactor
5. Annual gas use (therms/year)
BaselineGasUse = ConnectedLoad * EFLH / 100
Gas Savings Based on Equipment Efficiency
Inputs (cells with blue font)
6. Equipment efficiency
There parameters describe the efficiency of the baseline equipment currently installed and efficiency measure equipment to be installed
Retrieve data from Spec Sheet, if available, or contact manufacturer, if necessary
7. Data source
Provide data source(s) for the above efficiency values -- how were the values obtained, what documentation is available
Intermediate Results
8. Annual gas use (therms/year)
Baseline annual gas use should match the results shown in the Load Balance Tool
Efficiency measure annual gas use is calculated assuming:
a. Measure equipment has same input rating as baseline equipment
b. Measure equipment has same thermal load as baseline equipment
MeasureGasUse = BaselineGasUse * BaselineEfficieny / MeasureEfficiency
9. Gas savings (% of baseline)
Gas savings expressed as a percent of baseline gas use
GasSavings% = 1 - BaselineEfficieny / MeasureEfficiency
Final Result
10. Annual gas savings (therms/year)
Difference between annual gas use for baseline and efficiency measure
GasSavings = BaselineGasUse * (1 - BaselineEfficieny / MeasureEfficiency)
Cost Savings Based on Equipment Efficiency
Inputs (cells with blue font)
11. Gas rate ($/therm)
Customer gas rate
Final Result
12. Annual cost savings ($/year)
Customer cost savings resulting from annual gas savings
CostSavings = GasSavings * GasRate
Example of Savings Based on Equipment Efficiency
Gas Savings based on Gas Consumption per Unit of Production
Inputs (cells with blue font)
13. Gas consumed per unit of product (Btu/lb, Btu/gallon, Btu/unit of product)
To keep a record of the units used for gas consumption per unit of production (Btu/lb, kJ/L, Btu/gal, Btu/piece, SCF/unit of product), enter the units in the text box provided.
Enter the gas consumption per unit of product in the cells for the baseline equipment currently installed and efficiency measure equipment to be installed.
Retrieve data from Spec Sheet, if available, or contact manufacturer, if necessary
14. Data source
Provide data source(s) for the above values for gas use per unit of production -- how were the values obtained, what documentation is available
Intermediate Results
15. Annual gas use (therms/year)
Baseline annual gas use should match the results shown in the Load Balance Tool
Efficiency measure annual gas use is calculated assuming:
a. Measure equipment has same input rating as baseline equipment
b. Measure equipment has same thermal load as baseline equipment
MeasureGasUse = BaselineGasUse * MeasureGasUsePerUnit / BaselineGasUsePerUnit
16. Gas savings (% of baseline)
Gas savings expressed as a percent of baseline gas use
GasSavings% = 1 - MeasureGasUsePerUnit / BaselineGasUsePerUnit
Final Result
17. Annual gas savings (therms/year)
Difference between annual gas use for baseline and efficiency measure
GasSavings = BaselineGasUse * (1 - MeasureGasUsePerUnit / BaselineGasUsePerUnit)
Cost Savings based on Energy per Unit of Product
Inputs (cells with blue font)
18. Gas rate ($/therm)
Customer gas rate
Final Result
19. Annual cost savings ($/year)
Customer cost savings resulting from annual gas savings
CostSavings = GasSavings * GasRate
Example of Savings Based on Energy per Unit of Product
To keep a record of these results, Print the Calculator Page
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.