## Sheet1
Assumptions
Steam pressure typically 75 – 125 psig, 100 psig average
Atmospheric condensate return
Boiler efficiency 80%
Steam system operates 4000 hours per year
Typical trap ¾ “ float and thermostatic trap or balanced pressure thermostatic trap
Case 1 - energy saving calculation
Reference #4
¼ inch orifice (per Nicholson Steam Traps- N125 series)
Trap will not seat- 1/3 of orifice remains unobstructed for steam flow
0.016354 | sq. in. leakage area of orifice- 1/4 " diameter hole with leakage through 1/3 area
0.14434 | in. equivalent hole diameter
0.15625 | inch diameter for equivalent 5/32" diameter hole
700000000 | BTU annual steam loss (8760 hour operation) figure 10 Energy Loss through stem traps
875000000 | BTU annual fuel consumed @ 80 % boiler efficiency
8750 | therms
3995.4338 | therms loss for 4000 hours/ year operation (all steam is vented)
Case 2- energy saving calculation
Reference #3
11 traps replaced- |  | savings | 547 | kg/hr | 1203.4 | LBS/hr
109.4 | lbs/hr lost per trap
881 | btu/lb (enthalpy of evaporation)
96381.4 | btu/hr lost per trap
4819.07 | therms loss for 4000 hours/ year operation (enthalpy of evaporation lost to atmosphere)
Case 3- energy saving calculation
Reference #5
869 | traps leaking
111751570 | annual steam loss ( 8760 hours)
14.6801 | Lbs/ hr lost per trap
881 | btu/lb h fg
12933.19 | btu/hr lost per trap
646.6595 | therms loss for 4000 hours/ year operation (enthalpy of evaporation lost to atmosphere)
Case 4- energy saving calculation
Reference #6
steam pressure 100 psig
leak orifice diameter 1/8 inch, ( 1/4 " orifice with leakage area obstructed to 33%)
52.8 | lbs/hr (Leaking Steam trap Discharge Rate)
881 | btu/lb h fg
46516.8 | btu/hr lost per trap
2325.84 | therms loss for 4000 hours/ year operation (enthalpy of evaporation lost to atmosphere)
Lifetime
10 + years per Plant Engineering
Steam trap is automatic control valve-
Measure life is 15 years per CPUC Measure Life Table for controls ( automatic valves)
Cost