## Excess Air Tool
Gas Savings Calculation
Excess Air
Approach for Excess Air Reduction (select one)
Calculate Gas Savings for Power Burner or Combustion Air Damper
Repair furnace leaks for induced draft system
Repair furnace leaks for stack draft system
Parameter |  |  | Scenario
|  |  | Baseline | Efficiency Measure | Notes
Equipment Load and Annual Use Inputs
1. Connected load (MBtuh) |  |  | 50000 |  | Enter result from Report tab of Load Balance Program
2. Operating time (hrs/yr) |  |  | 7749 |  | Enter result from Report tab of Load Balance Program
3. Load Factor |  |  | 45% |  | Enter result from Report tab of Load Balance Program
4. Equivalent full load hours (hrs/yr) |  |  | 3487.05 |  | EFLH = OperatingTime * LoadFactor
5. Annual Gas Use (therms/yr) |  |  | 1743525 |  | BaselineGasUse = ConnectedLoad * EFLH / 100
Temperature and % Oxygen Inputs
6. Flue gas temperature (F) |  |  | 1600 | 1600 | Enter result from Flue Gas Test
7. Oxygen (O2) in flue gas (%, dry) |  |  | 4% | 2% | Enter result from Flue Gas Test
8. Combustion air temperature (F) |  |  | 80 | 80 | Obtain value from customer
Gas Savings for Power Burner or Combustion Air Damper
9. Excess air (%) |  |  | 22.15% | 9.607% | ExcessAir% = ftn(Oxygen %)
10. Annual gas use (therms/yr) |  |  | 1743525 | 1614897.5652 | MeasureGasUse = ftn(BaselineGasUse, FlueGasTemp, Oxygen%, and CombAirTemp)
11. Gas savings (%) |  |  | 7.377% |  | GasSavings% = ftn(FlueGasTemp, Oxygen%, and CombAirTemp)
12. Gas savings (therms/year) |  |  | 128627.4348 |  | AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Power Burner or Combustion Air Damper
13. Gas rate ($/therm) |  |  | 0.95 |  | Customer gas rate
14. Annual cost savings ($/year) |  |  | 122196.0631 |  | CostSavings = GasSavings * GasRate
Gas Savings from Reducing Air Infiltration on Induced Draft Combustion Systems
15. Induced draft (inches of W.C. of vacuum) |  |  | 0.2 |  | Obtain value from customer
16. Total opening area (square inches) |  |  | 36 | 0 | Obtain value from customer
17. Air infiltration (scfh) |  |  | 21580.0237 | 0 | AirFlow = ftn(OpenArea, Draft)
18. Annual gas use (therms/yr) |  |  | 1743525 | 1635924.8902 | MeasureGasUse = BaselineGasUse - AirFlow * OperatingTime * (Heat Required to Compensate for AirFlow)
19. Gas savings (%) |  |  | 6.171% |  | GasSavings% = 1 - MeasureGasUse / BaselineGasUse
20. Gas savings (therms/year) |  |  | 107600.1098 |  | AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Reducing Air Infiltration on Induced Draft Systems
21. Gas rate ($/therm) |  |  | 0.95 |  | Customer gas rate
22. Annual cost savings ($/year) |  |  | 102220.1043 |  | CostSavings = GasSavings * GasRate
Gas Savings from Reducing Air Infiltration on Stack Draft Combustion Systems
23. Stack height (from openings to top) (ft) |  |  | 20 |  | Obtain value from customer
24. Stack inside diameter (ft) |  |  | 4 |  | Obtain value from customer
25. Total opening area (square inches) |  |  | 36 | 0 | Obtain value from customer
26. Air infiltration (scfh) |  |  | 21299.7849 | 0 | AirFlow = ftn(OpenArea, Draft)
27. Annual gas use (therms/yr) |  |  | 1743525 | 1637322.1882 | MeasureGasUse = BaselineGasUse - AirFlow * OperatingTime * (Heat Required to Compensate for AirFlow)
28. Gas savings (%) |  |  | 6.091% |  | GasSavings% = 1 - MeasureGasUse / BaselineGasUse
29. Gas savings (therms/year) |  |  | 106202.8118 |  | AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Reducing Air Infiltration on Stack Draft Systems
30. Gas rate ($/therm) |  |  | 0.95 |  | Customer gas rate
31. Annual cost savings ($/year) |  |  | 100892.6712 |  | CostSavings = GasSavings * GasRate
Source: Calculation methodology provided by Arvind Thekdi, E3M, Inc.
Disclaimer The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.
Note on E11: Input: Connected load is Input Rating or Firing rate
Note on E12: Input: Annual operating time includes scheduled time the equipment is turned on but not using gas
Note on E13: Input: Load factor is EFLH as a percent of operating time
Note on E17: Input: Customer to measure this before reducing excess air. Generally flue gas temperatures are in the range 300-3,000 F. For flue gas temperatures between 200 and 300 F, the results below are less accurate, but within 5%.
Note on E18: Input: Customer to measure this before reducing excess air.
Note on F17: Input: Customer to measure this after reducing excess air.
Note on F18: Input: Customer to measure this after reducing excess air.

## Instructions
Instructions for
Excess Air Calculator
Select Approach for Excess Air Reduction
Selecting the appropriate button hides the inputs and results for the other approaches
Power Burner or Combustion Air Damper – This measure is to reduce the combustion air flow at the burner.
Induced Draft Leaks – This measure involves blocking leaks in the process heating system where ambient air is drawn into the system by an induced draft fan.
Stack Draft Leaks – This measure is similar to the induced draft case, except that the vacuum is caused by the draft effect created by the stack height.
Some of the user inputs are common to all measures.
Equipment Load and Annual Use Inputs (for all approaches)
Inputs (cells with blue font)
Use Load Balance Tool to determine these inputs
Customer supplied information that varies from the Load Balance Tool requires approval
1. Connected load (MBtuh)
Equipment input rating provided by the customer
May be available from the MAS database
2. Equipment operating time (hours/year)
3. Equipment load factor (equivalent full load hrs/yr as a percent of operating time)
Intermediate Results
4. Equivalent full load hours (hours/year)
EFLH = OperatingTime * LoadFactor
5. Annual gas use (therms/year)
BaselineGasUse = ConnectedLoad * EFLH / 100
Temperature and % Oxygen Inputs (for all approaches)
Inputs (cells with blue font)
Temperatures and oxygen concentration provided by customer measurements
6. Flue gas temperature (°F)
For combustion air preheat or excess air reduction, the baseline and efficiency measure flue gas temperatures are to be the same. Generally flue gas temperatures are in the range 300-3,000 F. For flue gas temperatures between 200 and 300 F, the results calculated here are less accurate, but within 5%.
7. Flue gas oxygen concentration (% by volume O2, dry basis)
For excess air reduction, the value should be lower for the efficiency measure than for the baseline.
8. Combustion air temperature (°F)
The baseline combustion air temperature is assumed to be ambient conditions.
For excess air efficiency measures, the combustion air temperature remains unchanged.
In no case should this temperature be higher than the flue gas temperature.
Gas Savings for Power Burner or Combustion Air Damper
Intermediate Results
9. Excess air (% of theoretical air)
Theoretical air is the exact quantity of air required for complete combustion.
Excess air % is calculated from the % O2 in the flue gas.
ExcessAir% = ftn(Oxygen %)
10. Annual gas use (therms/year)
Baseline is same value as above
MeasureGasUse = ftn(BaselineGasUse, FlueGasTemp, Oxygen%, and CombAirTemp)
11. Gas savings (% of baseline)
Gas savings expressed as a percent of baseline gas use
GasSavings% = ftn(FlueGasTemp, Oxygen%, and CombAirTemp)
Final Result
12. Gas savings (therms/year)
Difference between annual gas use for baseline and efficiency measure
AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Power Burner or Combustion Air Damper (optional)
Inputs (cells with blue font)
13. Gas rate ($/therm)
Customer gas rate
Final Result
14. Annual cost savings ($/year)
Customer cost savings resulting from annual gas savings
CostSavings = GasSavings * GasRate
Example of Savings for Power Burner or Combustion Air Damper
Gas Savings from Reducing Air Infiltration on Induced Draft Combustion Systems
Inputs (cells with blue font)
15. Induced draft (inches of W.C. of vacuum)
Obtain the vacuum pressure inside the combustion chamber, measured in inches of water column (IWC)
16. Total opening area (square inches)
Work with customer to measure the size of every opening into the vacuum in the baseline combustion chamber, calculate the area of each, and add them together. If there are any openings that cannot be blocked, re-measure their size after blocking the openings, calculate the area of each, and add them together for the entry in the efficiency measure column.
Intermediate Results
17. Air infiltration (scfh)
Total amount of air flowing into the combustion chamber before and after blocking the openings, expressed in standard cubic feet per hour
AirFlow = ftn(OpenArea, Draft)
18. Annual gas use (therms/year)
Baseline is same value as above, efficiency measure is new value
MeasureGasUse = BaselineGasUse - AirFlow * OperatingTime * (Heat Required to Compensate for AirFlow)
19. Gas savings (% of baseline)
Gas savings expressed as a percent of baseline gas use
GasSavings% = 1 - MeasureGasUse / BaselineGasUse
Final Result
20. Gas savings (therms/year)
Difference between annual gas use for baseline and efficiency measure
AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Reducing Air Infiltration on Induced Draft Systems (optional)
Inputs (cells with blue font)
21. Gas rate ($/therm)
Customer gas rate
Final Result
22. Annual cost savings ($/year)
Customer cost savings resulting from annual gas savings
CostSavings = GasSavings * GasRate
Example of Savings from Reducing Air Infiltration on Induced Draft Systems
Gas Savings from Reducing Air Infiltration on Stack Draft Combustion Systems
Inputs (cells with blue font)
23. Stack height (from openings to top) (ft)
Measure the stack height from the average height of the openings into the combustion chamber to the top of the stack
24. Stack inside diameter (ft)
Determine the average inside diameter of the stack. If the stack is not circular, use the hydraulic diameter = square root of (area in square feet times 4/p).
25. Total opening area (square inches)
Work with customer to measure the size of every opening into the vacuum in the baseline combustion chamber, calculate the area of each, and add them together. If there are any openings that cannot be blocked, re-measure their size after blocking the openings, calculate the area of each, and add them together for the entry in the efficiency measure column.
Intermediate Results
26. Air infiltration (scfh)
Total amount of air flowing into the combustion chamber before and after blocking the openings, expressed in standard cubic feet per hour
AirFlow = ftn(OpenArea, Draft)
27. Annual gas use (therms/year)
Baseline is same value as above, efficiency measure is new value
MeasureGasUse = BaselineGasUse - AirFlow * OperatingTime * (Heat Required to Compensate for AirFlow)
28. Gas savings (% of baseline)
Gas savings expressed as a percent of baseline gas use
GasSavings% = 1 - MeasureGasUse / BaselineGasUse
Final Result
29. Gas savings (therms/year)
Difference between annual gas use for baseline and efficiency measure
AnnualGasSavings = BaselineGasUse - MeasureGasUse
Cost Savings from Reducing Air Infiltration on Stack Draft Systems (optional)
Inputs (cells with blue font)
30. Gas rate ($/therm)
Customer gas rate
Final Result
31. Annual cost savings ($/year)
Customer cost savings resulting from annual gas savings
CostSavings = GasSavings * GasRate
Example of Savings from Reducing Air Infiltration on Stack Draft Systems
To keep a record of these results, Print the Calculator Page
Disclaimer
The Gas Company has made reasonable efforts to ensure all information is correct; however, neither The Gas Company's publication nor verbal representations thereof constitutes any statement, recommendation, endorsement, approval or guaranty (either express or implied) of any product or service. Moreover, The Gas Company shall not be responsible for errors or omissions in this publication, for claims or damages relating to the use thereof, even if it has been advised of the possibility of such damages.

## Excess Air (hidden)
To be hidden in final tool
Excess Air Calculation Tool
| Parameter | Scenario
|  | Baseline | Measure
| Equipment Load and Annual Use Inputs |  |  | Notes
| a. Input Rating (MBtuh) | 50000 |  | Enter result from Report tab of Load Balance Program
| b. Operating Time (hrs/yr) | 7749 |  | Enter result from Report tab of Load Balance Program
| c. Load Factor | 45% |  | Enter result from Report tab of Load Balance Program
| d. Equivalent Full Load Hours (hrs/yr) | 3487.05
| e. Annual Gas Use (therms/yr) | 1743525 |  | Verify annual gas use matches Load Balance Program
Temperature and % Oxygen Inputs
| a. Flue gas temperature (F) | 1600 | 1600 | Should be equal, except with combustion air preheat
| b. Oxygen (O2) in flue gas (%, dry) | 4% | 2% | Enter percent as whole number (2, not .02)
| c. Combustion air temperature (F) | 80 | 80 | Both columns must be less than flue gas temperature
| d. Excess air (%) | 22.15% | 9.607% | Percent of theoretical air
| e. Available Heat to Process (%) | 47.87% | 51.68% | Losses other than flue gas losses are included in available heat
Gas Savings Results
| a. Gas savings (%) | 7.377%
| b. Annual Gas Use (therms/year) | 1743525 | 1614897.5652
| c. Gas Savings (therms/year) | 128627.4348
Calc Table: Do Not Delete
| Source: Arvind Thekdi, EC3M | Base | EE Measure
| Stoichiometric Available Heat Calc | 55 | 55
| Excess Air Adjustment | -6.6447 | -2.8822
| Combustion Air Preheat Adjustment | -0.4886 | -0.43843
| Final Available Heat Numbers | 47.8667 | 51.6793

## Induced Draft Tool (hidden)
To be hidden in final tool
Induced Draft Air Infiltration Calculation Tool
| User Inputs |  |  | Baseline | Efficiency Measure
Input Rating (MBtuh)
| Operating Time (hours/year) |  |  | 7749 | 7749
Load Factor
| Temperature of flue gases (F) |  |  | 1600 | 1600
| % Oxygen in flue gases |  |  | 4% | 2%
| Combustion air temperature (F) |  |  | 80 | 80
| Furnace draft (neg. pressure) inch. W.C. |  |  | 0.2 | 0.2
| Opening size - area sq.in. |  |  | 36 | 0
Assumptions
** Assume 1 scf flue gas produced for 95 Btu heat release by combustion
Air infiltration from openings vs. negative pressure or draft
x=inch w.c. negative pressure
| f (x) = | air flow cfh/sq. inch
6.857
+ 7089.3291893336955 * x
- 38037.10178718846 * x^2
+ 108378.65837904214 * x^3
- 111188.81118930216 * x^4
Model Inputs
in. w.c. | flow cfh/in^2
x | y |  | Coef.
0.1 | 423.8717 | C1 | 1340.4 | sqrt(x)
0.2 | 599.4451
0.3 | 734.1673
0.4 | 847.7434
| Avg. Heat |  | 95 | -0.025
| Excess air correction |  | -2 | 0.02
| Preheated air correction |  | -2 | 0.02
Excess Air vs. % O2
|  | Co | 0.0258
|  | C1 | 3.7855 | x
|  | C2 | 0.60844 | x^2
|  | C3 | -0.062753 | x^3
|  | C4 | 0.0049281 | x^4
Intermediate Results
| flow cfh/in^2 |  |  | 599.4451 | 599.4451
| Air infiltration SCFH |  |  | 21580.0237 | 0
| Heat reqd. (net) to heat air Btu/hr. |  |  | 664664.7307 | 0
| Excess Air |  |  | 22.1483 | 9.6074 | %
| Avg. Heat 1 |  |  | 55 | 55
| Excess Air Correction |  |  | -6.6445 | -2.8822
| Preheat Air Correction |  |  | -0.48859 | -0.43843
| Available Heat |  |  | 47.8669 | 51.6794 | % of gross Heating Value
| Gross heat reqd. btu/hr |  |  | 1388567.6838 | 0
Final Results
| Fuel wasted therms per year |  |  | 107600.1098 | 0
| Annual gas use (therms/year) |  |  | 1743525 | 1635924.8902
| Annual gas savings (%) |  |  | 6.171%
| Annual gas savings (therms/year) |  |  | 107600.1098
|  |  | check | 266846

## Stack Draft Tool (hidden)
To be hidden in final tool
Stack Draft Air Infiltration Calculation Tool
Parameter
|  |  |  | Baseline | Efficiency Measure
Equipment Load and Annual Use Inputs
| Input Rating (MBtuh) |  |  | 50000 | 50000
| Operating Time (hours/year) |  |  | 7749 | 7749
Load Factor
Temperature and % Oxygen Inputs
| Temperature of flue gases (F) |  |  | 1600 | 1600
| % Oxygen in flue gases |  |  | 4% | 2%
| Combustion air temperature (F) |  |  | 80 | 80
Stack Draft Inputs
| Stack Height (openings to top) (ft) |  |  | 20 | 20
| Stack Inside Diameter (ft) |  |  | 4 | 4
| Total Opening Area (sq. in.) |  |  | 36 | 0
Assumptions
** Assume 1 scf flue gas produced for 95 Btu heat release by combustion
Air infiltration from openings vs. negative pressure or draft
x=inch w.c. negative pressure
| f (x) = | air flow cfh/sq. inch
6.857
+ 7089.3291893336955 * x
- 38037.10178718846 * x^2
+ 108378.65837904214 * x^3
- 111188.81118930216 * x^4
Model Inputs
in. w.c. | flow cfh/in^2
x | y |  | Coef.
0.1 | 423.8717 | C1 | 1340.4 | sqrt(x)
0.2 | 599.4451
0.3 | 734.1673
0.4 | 847.7434
| Avg. Heat |  | 95 | -0.025
| Excess air correction |  | -2 | 0.02
| Preheated air correction |  | -2 | 0.02
Excess Air vs. % O2
|  | Co | 0.0258
|  | C1 | 3.7855 | x
|  | C2 | 0.60844 | x^2
|  | C3 | -0.062753 | x^3
|  | C4 | 0.0049281 | x^4
Intermediate Results
| CFS of flue gas at temp. t (F) ** |  |  | 580.2817 | 580.2817 | 59F air
| Density of flue gases lb./ft^3 |  |  | 0.019311 | 0.019311 | 60F air temp, 0.0765 lb/scf flue gas
| Theoretical draft inch w.c. |  |  | 0.21934 | 0.21934
| Frictional loss in stack (inch of w.c.) |  |  | 0.024499 | 0.024499
| Effective draft inch. W.c. |  |  | 0.19484 | 0.19484
| flow cfh/in^2 |  |  | 591.6607 | 591.6607
| Air infiltration SCFH |  |  | 21299.7849 | 0
| Heat reqd. (net) to heat air Btu/hr. |  |  | 656033.3762 | 0
| Excess Air |  |  | 22.1483 | 9.6074 | %
| Avg. Heat 1 |  |  | 55 | 55
| Excess Air Correction |  |  | -6.6445 | -2.8822
| Preheat Air Correction |  |  | -0.48859 | -0.43843
| Available Heat |  |  | 47.8669 | 51.6794 | % of gross Heating Value
| Gross heat reqd. btu/hr |  |  | 1370535.7057 | 0
Final Results
| Fuel wasted therms per year |  |  | 106202.8118 | 0
| Annual gas use (therms/year) |  |  | 1743525 | 1637322.1882
| Annual gas savings (%) |  |  | 6.091%
| Annual gas savings (therms/year) |  |  | 106202.8118
188909