QUESTION TURN-TCAP-PSEP-04-01:

The responses to DRA Data Request DAO-2, question 14 and DAO-30, question 1 refer to lines that have been pressure tested as part of the Transmission Integrity Management Program (TIMP) or as additional projects not part of the TIMP assessment activities.

  - For each pressure test undertaken as part of the TIMP, please indicate whether the test identified any leak or other condition that required repair. For each such leak or other condition, please describe the nature of the leak (pin-hole, etc.) and the amount of time required to perform the repair.

  - For each pressure test undertaken as part of the TIMP, please indicate the amount of time that the line was out of service for pressure testing.

  - For each pressure test undertaken as part of the TIMP, please identify whether there were customer outages or any other disruption to service to utility customers and, if so, describe those outages in terms of the number of customers who experienced a disruption, the duration of the disruption, and the steps the utility took to minimize and mitigate the disruption.

  - For each pressure test on an existing line that was not part of the TIMP assessment activities, please indicate whether the test identified any leak or other condition that required repair. For each such leak or other condition, please describe the nature of the leak (pin-hole, etc.) and the amount of time required to perform the repair.

  - For each pressure test on an existing line that was not part of the TIMP, please indicate the amount of time that the line was out of service.

  - For each pressure test on an existing line that was not part of the TIMP, please identify whether there were customer outages or any other disruption to service to utility customers and, if so, describe those outages in terms of the number of customers who experienced a disruption, the duration of the disruption, and the steps the utility took to minimize and mitigate the disruption.

RESPONSE TURN-TCAP-PSEP-04-01:

- To date, pressure tests undertaken as a part of TIMP have identified no instances of leaks or failures directly related to pipeline material.  There have been three instances of leakage occurring on the temporary equipment installed to facilitate the tests (one leak at a gasket in a flange assembly and two leaks related to faulty valves), but these leaks are not representative of hydrotest failures.

| Pipeline | Duration of Outage | Comments |
| --- | --- | --- |
| 1229 | 10/16/06 to 11/17/06 | This is the time frame when the main line was tested and the entire line placed back in service. Other smaller retro-fit sections were tested on separate occasions. |
| PGR6 group | 1/26/10 to 6/14/10 | Storage field piping. |
| 80 | Approx. March to July, 2010 | The pressure test was part of much larger project to assess all of Line 80. |
| 324 | * | *Data not readily available. Pressure test for new pipeline segment was part of much larger assessment project, and dates are co-mingled with other work. |
| 6906 | N/A | Commissioning pressure test for new pipeline. |
| 44-137 | * | *Data not readily available |

- TIMP related pressure tests have been limited to pipeline systems that lend themselves to avoidance of service disruptions, and as a result there are no examples of TIMP related hydrotest outages or disruptions.

- Of the three pipelines identified in DRA-DAO-30-1, only one of, the hydrotests on Line 6906 S, resulted in a leak (a single leak at a small girth weld crack).  Due to the minor nature of the leak combined with its logistically difficult location, discovery and positive identification of its exact location was an unusually lengthy process (approximately 3.5 months).  Once located, repair of the leak took approximately 2 days to complete.

| Pipeline | Duration of Outage | Comments |
| --- | --- | --- |
| 4000 | 10/26/07 |  |
| 6916 S | N/A | This was a commissioning effort; no associated outage occurred since the line was not yet in-service. |
| 1022 | 11/7/11 to 11/17/11 | Service to power plant. Pressure test was conducted during planned outage. |

- No service disruptions related to the pipelines listed in TURN-TCAP-PSEP-04-01e above were experienced.

QUESTION TURN-TCAP-PSEP-04-02:

The response to Indicated Producers (IP)/Watson Cogeneration (Watson) Data Request IP-2, question 1 refers to the installation of bypass piping as an action that could be taken to minimize service interruptions.

  - Please describe in greater detail what the installation of bypass piping entails and the conditions under which such bypass piping is a reasonable option.

  - Have the utilities previously installed bypass piping in order to minimize service interruptions from pipeline maintenance or other activities that might otherwise cause service interruptions?  If so, please describe in detail the utilities’ experience with such bypass piping.

  - For each year from 2005-2011, inclusive, please state the number of times the utilities have installed bypass piping.  For each such use of bypass piping, please state the length of bypass piping installed, the number of customers served by that bypass piping, and the total load of the customers served by that bypass piping.

  - Please describe the ratemaking and cost recovery treatment applied to the costs associated with installing bypass piping, including but not limited to whether the costs are treated as O&M expense versus capitalized, and the FERC account (under the Uniform System of Accounting) in which the costs are recorded.  If any portion of the bypass piping cost is capitalized, please state the average service life assumed for depreciation purposes.

RESPONSE TURN-TCAP-PSEP-04-02

- A typical bypass consists of temporary piping that is fabricated aboveground to maintain gas flow through an existing pipeline at the point where a section of line, fitting, or valve is being removed and replaced. The temporary piping is connected to the existing pipeline with special fittings that are welded to the pipeline. The fittings are designed to accommodate complex tools that divert the flow of gas into the bypass piping and permit the replacement of the obsolete material.   Through the bypass, the work can be completed without service interruption to customers.  The temporary piping is modeled and sized to meet the minimum requirements to ensure continued service to customers. A bypass requires that sufficient workspace be available to fit the temporary facilities in a safe manner, and allow the retrofit work to be performed. Therefore, a bypass cannot always be designed and fabricated to fit every worksite.

- Refer to c) below.

- For the period 2005-2011, the utilities have installed more than 25 bypasses on pipeline retrofit projects.  These temporary facilities have ranged from 40 ft. to 250 ft. in length.  Typically, the bypasses have avoided the curtailment of large numbers of residential and commercial customers, not a specific customer. Determining the exact number of customers and the total load supported through a bypass for each of these projects is not possible in all cases and will require several weeks to assemble.

- For transmission projects, permanent bypass piping costs would be recorded to FERC 367 Transmission Mains which currently has an average service life of 55 years.

QUESTION TURN-TCAP-PSEP-04-03:

At page 55 of the Amended Testimony, the Sempra Utilities state “a preliminary review was completed to determine if the pipeline could be taken out of service for a period of 2 to 6 weeks to complete pressure testing.”

  - Please describe in detail the basis for the 2-6 week period used for the preliminary review.  Please also provide all documents that set forth the basis for this period of being out of service.

  - Please describe in detail the “preliminary review” referred to in the testimony, including but not limited to the persons involved in that preliminary review, the instructions or direction provided to those persons regarding the preliminary review, and the results of that preliminary review.   Please also provide all documents regarding the preliminary review, including but not limited to the selection of the persons who performed the review, the instructions or directions provided to those persons, and the results of the preliminary review.

RESPONSE TURN-TCAP-PSEP-04-03

- A time period of 2–6 weeks to complete pressure testing was used as a general guideline to assist in the high level forecast of the PSEP replacement and pressure test scope.  Considering the basic activities and logistics involved in a pressure test, such as installation of necessary valves/test heads, installation of fill and de-water piping, gas handling, filling, pressure testing, de-watering site preparation with containment and storage tanks, minor leak detection and repair, de-water after test, and tie facilities back into existing piping system infrastructure, company subject matter experts believe 2–6 weeks is a reasonable general assumption for project duration.

As each line and segment has unique characteristics, further definition and substantiation of pressure testing scope and schedule will be determined after development of engineering, design, and execution planning.

- The preliminary reviews consisted of high level analyses regarding the ability to take pipelines identified in the PSEP out of service for pressure testing with manageable customer impacts.  These reviews were performed by subject matter experts and operations personnel most familiar with the SoCalGas/ SDG&E systems and best equipped with the knowledge to make high level judgments regarding which segments can be taken out of service for pressure testing with manageable customer impacts.

Below is the process the Sempra Utilities followed when input was sought from regional field services groups during the development of the proposed scope of work:

- background was provided to each of the field services groups on the PSEP in general and the overall objective;

- files and templates with the line numbers and segments with categories and criteria miles were provided to the field services groups;

- there were weekly meetings to review status and ask questions;

- there was a feedback loop to promote discussion.

Guidance was provided to the field services groups to assist in their analysis and response.  First, field services was informed that the PSEP applies to all DOT transmission miles, but does include a priority scope.  Field services was informed that an overall assumption was made that if a segment (as defined by a work order) has any category 4 criteria mileage then field services was to assume the entire segment would be remediated.  Field services was also asked to consider the promotion of standardize pipe diameters and piggability. Field services were then asked to determine if the category 4 criteria segments could be taken out of service to be hydrotested or would need to be replaced.

To enhance TURN’s understanding of the process, attached please find the emails sent by the central project management group to the regional field offices.  Also attached are the responses received from the regional groups.  Please note that because these e-mails were sent very early in the process of developing the scope of work, much of the data in the spreadsheet attachments (categories, % SMYS, class, grade, wall thickness, installation dates, internal notes, etc.) may not be consistent with what was provided in the final work-product included in testimony/work papers (e.g. these are “work-in-progress” pieces of correspondence).  Up until August 26, the Sempra Utilities continued to review, check, revise and then format the information that was ultimately included in the workpapers.  Note these emails were provided to DRA on 4/9/12 as a follow up to a briefing on the PSEP.

QUESTION TURN-TCAP-PSEP-04-04:

The response to DRA DAO-20, question 4 states, in part, “if during the engineering, design, and execution planning phases of the PSEP it is determined that a segment, or segments, of pipe proposed for replacement in the PSEP filing can be taken out of service and pressure tested in a more cost effective manner than replacement, those segments will be instead be pressure tested.”

  - Please describe in detail how the Sempra Utilities would determine that a segment of pipe proposed for replacement can be taken out of service and pressure tested in a more cost effective manner than replacement.

  - Please identify and describe all factors that the Sempra Utilities anticipate considering in making the determination that a segment of pipe might be taken out of service and pressure tested in a more cost-effective manner.

RESPONSE TURN-TCAP-PSEP-04-04 (provided separately to TURN on 6/11/12)

- SoCalGas/SDG&E are currently in the process of developing the criteria that will be used to determine whether a pipeline should be replaced or whether it can be taken out of service for pressure testing with manageable customer impacts.  It is anticipated that this criteria will be included in rebuttal testimony.

- See response 04-04(a) above.  See also Response DRA-DAO-07-1 for some of the factors that may be included in the final criteria.  The factors identified in this data request response are not intended to be an all-inclusive list.

QUESTION TURN-TCAP-PSEP-04-05:

At pages 85-86 of the Amended Testimony, the Sempra Utilities describe the installation of fiber optic right-of-way monitors to help identify when intrusions into their pipeline rights-of-way have occurred or when a pipeline (or right-of-way) has experienced movement that might pose a threat to pipeline structural integrity.

  - Please explain in detail why the Sempra Utilities selected fiber optic right-of way monitors to serve the functions described in the testimony.

  - Please identify and describe other existing technology options that the Sempra Utilities considered to serve the functions described in the testimony (as opposed to the “emerging technology” options addressed on page 86).

  - Please describe in detail how the Sempra Utilities analyzed the various existing technology options considered to serve the functions described in the testimony.

Please provide all documents associated with the Sempra Utilities analysis of the various existing technology options considered to serve the functions described in the testimony.

RESPONSE TURN-TCAP-PSEP-04-05

- Sempra selected continuous fiber optic right-of-way monitors for newly-installed pipelines, because it believes such technology, at the present time, offers the best and most cost-effective path for accurately detecting when and where significant activity on a along a pipeline right-of-way is occurring.    This technology can pinpoint right-of-way disturbances BEFORE a pipeline is actually impacted, allowing for preventative intervention by utility personnel.  When evaluating a potential situation, one would first see fiber disturbance, possibly followed by severance of the fiber optic cable (an event requiring no sophisticated algorithms to interpret), which would then provide secondary confirmation.  These two series of events would precede equipment striking the pipeline.

Some alternate technologies are dependent upon the impact of the pipeline under protection to provide operator notification of a problem which may have already occurred.  Fiber optic cabling installed above the pipeline would allow for earlier detection of an impending, as opposed to contemporaneous compromise of the pipeline.

- Sempra believes fiber-based systems represent the most reliable and accurate of the right-of-way/intrusion technologies currently commercially available.  It also represents a technology for which other valued applications are within technical reach, including leak detection, video survey of pipelines, and high resolution strain gauge configuration for special facilities or geologic areas.  Unfortunately, retrofitting pipelines with fiber optic cabling/mesh in congestion areas is both cost and logistically challenging.  In such cases, SoCalGas/SDG&E will wait and continue to test acoustic-based or other type intrusion systems in hopes that this technology can yield consistent results when deployed in complex network pipelines in a city environment.  SoCalGas had tested some preliminary acoustic monitoring technology several years ago and noted some gaps in applicability to its pipeline operations, even in remote locations.

Other technology options included:

- Video cameras

- Increased aerial survey

- Satellite imagery

Potential acoustic monitoring links are provided below:

http://www.ge-energy.com/content/multimedia/_files/downloads/ThreatScan.pdf

http://www.aiworldwide.com/pigpenoverview

In addition, SoCalGas/SDG&E are looking at more than one fiber optic solution. The below links provide information on several under consideration:

http://www.ussensorsystems.com/oil-gas-overview.html

http://www.fiberpatrol.com/fp6000.php

http://www.fftsecurity.com/secure_pipe_pipeline_intrusion_detection_system.php

http://www.ozoptics.com/ALLNEW_PDF/APN0010.pdf

http://www.omnisens.ch/ditest/3411-pipelines-pim.php

- Analysis came through several processes:

- Detailed discussion with vendors, and small scale demonstrations at vendor locations;

- Discussion with industry research operatives;

- Participation in research consortiums and related verbal feedback;

- White paper and/or vendor literature review;

- Historical use of acoustic monitoring deployment in SoCalGas.

There are no detailed SoCalGas/SDG&E documents or reports available. SoCalGas/SDG&E hope to field test fiber optic and possibly acoustic monitoring-type equipment in 2013.

QUESTION TURN-TCAP-PSEP-04-06:

In Attachment A to the “Comments of Southern California Gas Company and San Diego Gas & Electric Company In Response to Assigned Commissioner’s Rulings and Supplement to Request for Memorandum Account” filed and served on January 13, 2012, the utilities list a number of pipelines by “PSEP Filing Priority” and with a cost estimate stated as either capital or O&M.

  - For each of the pipelines for which an O&M cost estimate is provided, please confirm that the utilities’ estimate is based on pressure testing the pipeline rather than replacing it.

  - For each of the pipelines for which an O&M cost estimate is provided, please identify those for which SoCalGas or SDG&E identified a negative customer impact from pressure testing.

  - For each of the pipelines for which an O&M cost estimate is provided, please identify the mitigation measure, if any, to reduce or minimize the customer impact from pressure testing.

RESPONSE TURN-TCAP-PSEP-04-06

- For each pipeline that has an O&M cost estimate in Attachment A, the proposed action for that pipeline in Phase 1A is pressure testing.

- Most, if not all, projects executed as part of the PSEP will have some degree of customer impact.  For those projects proposed in the PSEP for pressure testing, the impacts are anticipated to be manageable over the estimated 2 – 6 week period necessary to conduct the pressure test.  Reference Response DRA-DAO-07-1 for a discussion of manageable customer impacts.

- Final determination of all customer impacts and the applicable mitigation strategies for these impacts have not yet been determined and will be evaluated as part of the engineering, design, and project execution planning (See Response DRA-PZS-07-8).  Response DRA-DAO-07-1 identifies several mitigation measures that were considered when the high level PSEP scope of work was being developed.