QUESTION DAO7-1:

In Figure IV-1, on page 61, the proposed decision tree shows the question, “Can pipeline be taken out of service with manageable customer impact?” (See Box B). Please define “manageable customer impact” as used in the question and identify the list of criteria used to determine whether a segment can be taken out of service.

RESPONSE DAO7-1:

Manageable customer impact means an acceptable level of negative effects to our customers as a result of the PSEP.  Please refer to the discussion of reliability of service to customers on page 35 of the Testimony.  The criteria used to determine whether a segment can be taken out of service varies based upon specific pipeline and local system characteristics that may include, but are not limited to system looping and flexibility; impact to capacity; curtailment to non-core customers; impact to shippers, customers, and the gas market; availability of alternate sources of gas; anticipated outage duration; and the ability to mitigate these negative impacts through construction of parallel systems.

QUESTION DAO7-2:

In Sempra’s workpapers, Appendices IX-1-A through D, for pipeline replacement and pressure test costs, Sempra uses SPEC’s estimates for the materials, construction, and design/engineering/construction/environment for each pipeline segment in the proposed safety enhancement plan.  Please provide the following information regarding the SPEC estimates.

  - Has Sempra performed a comparison of SPEC’s cost estimates to any other sources?  If yes, please provide a copy of all comparisons performed.

  - Has Sempra performed a comparison of SPEC’s cost estimates to 2011 industry costs for materials, construction, and engineering services for pipeline replacements or for pressure testing as they relate to transmission and distribution pipes?  If yes, please provide a copy of all documents and calculations used in the comparisons.  If no, please provide a detailed explanation and clearly state the reasons why no cost comparisons were made.

  - Has Sempra performed a comparison of SPEC’s cost estimates versus Sempra’s recorded costs for materials, construction, and engineering services for pipeline replacements or for pressure testing as they relate to transmission and distribution pipes?  If yes, please provide a copy of all documents and calculations used in the comparisons.  If no, please provide a detailed explanation and clearly state the reasons why no cost comparisons were made.

RESPONSE DAO7-2:

- A comparison of SPEC’s cost estimates to other sources was not performed.  Updated and detailed cost estimates based on evaluated vendor and contractor quotations will be prepared after detailed engineering/design and execution planning has been completed.

- A comparison of SPEC’s cost estimates to 2011 industry costs has not been performed.  However, as explained in Appendices D and E of the testimony and communicated in the October 12th conference call, SPEC’s material and construction costs and labor rates are based on current industry pricing.

- SoCalGas and SDG&E did not perform a detailed comparison of company historical costs to SPEC’s materials, construction, and engineering costs provided in their estimates.  One of the motivations to utilize a reputable, southern California based pipeline engineering company was to get an experienced, independent, 3rd party perspective on the cost to replace or pressure test pipe segments.  SPEC Services has the resources and capability to collect up-to-date industry pricing, whereas SoCalGas and SDG&E’s historical projects and costs may not be indicative of the current materials, construction, and labor costs.

QUESTION DAO7-3:

On page 3 of the testimony, Sempra states, “Because we have already invested in an ambitious in-line inspection program as part of our existing pipeline integrity management program, many of the pipelines identified for testing or replacement are already retrofitted to allow for in-line inspection.”  Please answer the following questions with regard to this statement:

- Please define “pipeline integrity management program” as referenced above.

- Please identify the number of miles, and specific line segments, proposed for replacement and for pressure testing in the PSEP that are being assessed and or managed or included in the existing pipeline integrity management program referenced above.

- For each of the specific line segments identified in 3(b) above, please identify the dates that each line was assessed, re-assessed, or scheduled for assessment, as part of the pipeline integrity management program.

- For each of the specific line segments identified in 3(b) above, please provide a copy of all assessments performed as part of the pipeline integrity management program and a copy of the recommendations associated with these assessments.

- For each of the specific line segments identified in 3(b) above, please identify the specific actions taken to improve the safety and reliability of pipeline systems, as intended by the mandates of the pipeline integrity rules found in the Code of Federal Regulations (CFR) 49 C.F.R. Section 192.901 Subpart O.

- For each of the line segments identified in 3(b) above, please (1) identify the safety and reliability improvements, as a direct result of work activities performed under the integrity management program, (2) explain in detail how Sempra measured the specific safety and reliability improvements, and (3) identify the metrics used to measure improvements.

- For each of the line segments indentified in 3(b) above, please explain in detail how Sempra addressed all the elements of pipeline integrity management as they pertain to the 49 C.F.R. Section 192.901 Subpart O “Gas Transmission Pipeline Integrity Management.”

h.	Provide a copy of all submitted reports regarding the overall performance measures of the pipeline integrity management program in accordance with §192.951 and §192.945.

RESPONSE DAO7-3:

- Please refer to page 38 of the Testimony for a complete discussion of Gas Transmission Integrity Management.

- In-progress.  Completion of response is estimated for November 23rd, 2011.

- In-progress.  Completion of response is estimated for November 23rd, 2011.

- Assessments are performed in compliance with the requirements of CFR 49, Subpart O §192.921.  The assessment methods used by SoCalGas and SDG&E include direct assessment, pressure testing, and in-line inspection as referenced in 49 C.F.R. Subpart O.  While it is infeasible and unduly burdensome to include a copy of all assessments conducted as part of the integrity management program, the findings resulting from performance of an integrity assessment must comply with the requirements §192.933(c).  These requirements are given as follows:

An operator must complete remediation of a condition according to a schedule that prioritizes the conditions for evaluation and remediation. Unless a special requirement for remediating certain conditions applies, as provided in paragraph (d) of this section, an operator must follow the schedule in ASME/ANSI B31.8S (ibr, see §192.7), section 7, Figure 4. If an operator cannot meet the schedule for any condition, the operator must justify the reasons why it cannot meet the schedule and that the changed schedule will not jeopardize public safety.

Requirements addressing the findings resulting from assessments are provided in §192.933(d) as follows:

(1)  Immediate repair conditions. An operator's evaluation and remediation schedule must follow ASME/ANSI B31.8S, Section 7 in providing for immediate repair conditions. To maintain safety, an operator must temporarily reduce operating pressure in accordance with paragraph (a) of this section or shut down the pipeline until the operator completes the repair of these conditions. An operator must treat the following conditions as immediate repair conditions:

(i). A calculation of the remaining strength of the pipe shows a predicted failure pressure less than or equal to1.1 times the maximum allowable operating pressure at the location of the anomaly. Suitable remaining strength calculation methods include, ASME/ANSI B31G ("Manual for Determining the Remaining Strength of Corroded Pipelines" (1991); AGA Pipeline Research Committee Project PR-3-805 ("A Modified Criterion for Evaluating the Remaining Strength of Corroded Pipe" (December 1989)); or an alternative equivalent method of remaining strength calculation. These documents are incorporated by reference and available at the addresses listed in Appendix A to Part 192.

(ii)  A dent that has any indication of metal loss, cracking or a stress riser.

(iii) An indication or anomaly that in the judgment of the person designated by the operator to evaluate the assessment results requires immediate action.

(2)  One-year conditions. Except for conditions listed in paragraph (d)(1) and (d)(3) of this section, an operator must remediate any of the following within one year of discovery of the condition:

(i)  A smooth dent located between the 8 o'clock and 4 o'clock positions (upper 2/3 of the pipe) with a depth greater than 6% of the pipeline diameter (greater than 0.50 inches in depth for a pipeline diameter less than Nominal Pipe Size (NPS) 12).

(ii)  A dent with a depth greater than 2% of the pipeline's diameter (0.250 inches in depth for a pipeline diameter less than NPS 12) that affects pipe curvature at a girth weld or at a longitudinal seam weld.

(3)  Monitored conditions. An operator does not have to schedule the following conditions for remediation, but must record and monitor the conditions during subsequent risk assessments and integrity assessments for any change that may require remediation:

(i)  A dent with a depth greater than 6% of the pipeline diameter (greater than 0.50 inches in depth for a pipeline diameter less than NPS 12) located between the 4 o'clock position and the 8 o'clock position (bottom 1/3 of the pipe).

(ii)  A dent located between the 8 o'clock and 4 o'clock positions (upper 2/3 of the pipe) with a depth greater than 6% of the pipeline diameter (greater than 0.50 inches in depth for a pipeline diameter less than Nominal Pipe Size (NPS) 12), and engineering analyses of the dent demonstrate critical strain levels are not exceeded.

(iii)  A dent with a depth greater than 2% of the pipeline's diameter (0.250 inches in depth for a pipeline diameter less than NPS 12) that affects pipe curvature at a girth weld or a longitudinal seam weld, and engineering analyses of the dent and girth or seam weld demonstrate critical strain levels are not exceeded. These analyses must consider weld properties.

- While it is infeasible and unduly burdensome to provide all actions taken as a result of integrity assessments conducted, actions taken as a result of integrity assessments are addressed per the requirements provided in §192.933(d).  SoCalGas and SDG&E’s repair procedures conform to those requirements.  Repair methods typically include (but are not limited to) pressure reduction, repair with a band or sleeve, grinding, replacement, and recoating.  An exhaustive listing of prevention and repair methods is provided in Table 4 of ASME B318.S-2010.

- (1) Please see answer 7-3(e) above.

(2) Integrity management program performance is measured in accordance with the requirements in §192.945.  These include the overall performance measures specified in AMSE B318.S, section 9.4, and the specific measures for each identified threat specified in Appendix A of the same standard.  External corrosion direct assessment program measures as required under 49 CFR Part 192.945(b) are contained within the SoCalGas and SDG&E procedure for ECDA assessments.

(3) The metrics used to measure improvements resulting from the integrity management program are contained in the reports provided in response to question 7-3(h).

- SoCalGas and SDG&E developed a written Integrity Management Plan in accordance with Section 192.907(a) that addresses the elements contained within 192.911.

- See attached integrity management program performance reports.

QUESTION DAO7-4:

Referring to Sempra’s statement on page 50 of the testimony, “First, Phase 1 A, all transmission pipelines in populated areas that do not have sufficient documentation to validate a post-construction pressure test of at least 1.25 MAOP are scheduled to be addressed.”  Please answer the following questions with regard to this statement:

  - Please explain in detail what is meant by, “do not have sufficient documentation to validate a post-construction pressure test…”

  - Please explain in detail why Sempra does not have sufficient documentation to validate a post-construction pressure test of at least 1.25 MAOP.

  - Please identify the documents that Sempra should have had in order to validate a post-construction pressure test of at least 1.25 MAOP.

  - Does Sempra have the MAOP for each of the line segments identified in Phase 1A for either pressure testing or for replacement?

  - How did Sempra determine the MAOP for each of the lines identified in Phase 1A for either pressure testing or for replacement?

  - Please identify the documents validating at least 1.25 MAOP that Sempra currently has for each line segment it is seeking to pressure test or to replace in this application, as identified in workpapers, Appendix IX-1-A and Appendix IX-1-B.  For each document provided, please identify the name of the document, a brief summary of the details contained in the record, and a statement describing how and where this document/record is being kept and its accessibility.

  - The pipeline integrity management rule for gas transmission (TIMP) focuses on a subset of the transmission system, HCAs, that are high in population density areas.  How many of the proposed miles, for pipeline replacement and for pressure testing, as presented on page 5 of the testimony, are part of the miles required to be maintained under TIMP?

  - For each of the TIMP miles in question 4(g) above, please identify the type of records required to be maintained by DOT’s pipeline integrity rules found in the 49 C.F.R. Section 192.901 Subpart O “Gas Transmission Pipeline Integrity Management.”

RESPONSE DAO7-4:

- The detailed description of the criteria used for determination of “sufficient documentation to validate a post-construction pressure test” is described on page 9 of the April 15th, 2011 Report of Southern California Gas Company and San Diego Gas & Electric Company on Actions Taken in Response to NTSB Safety Recommendations.

- Please see response DAO 2-9.

- The records review process, and the criteria for sufficient documentation to meet the NTSB’s Safety Recommendations to PG&E and/or the requirements of D.11-06-017 is detailed in the April 15th, 2011 Report of Southern California Gas Company and San Diego Gas & Electric Company on Actions Taken in Response to NTSB Safety Recommendations.

- Yes

- All pipelines installed prior to July 1, 1970 have MAOPs established either by design and test pressure or by design and operating pressure histories. All pipelines installed after June 30, 1970, have MAOPs established by design and test pressure only.

- Lines identified for pressure testing or replacement within this plan do not have records sufficient to validate a pressure test of at least 1.25 MAOP was performed.  For each line within the PSEP, the types of post-construction records reviewed to validate MAOP include the following:

| Record | Summary | Media/Location | Accessibility |
| --- | --- | --- | --- |
| As-built drawings | Drawing of the pipeline installation with pressures from the Strength Test | Hard copies/ Field office line files | Physical review |
| Pressure Test Charts | Pressure test charts record the pressures achieved during the strength test | Hard copies/ Field office line files | Physical review |
| Design Data Sheet | Listing of material properties with maximum, minimum, and actual test pressures | Hard copies/ Field office line files | Physical review |
| Hydrostatic Test Log | Listing of pressures during a hydrostatic pressure test | Hard copies/ Field office line files | Physical review |

- Please see DAO-7-3b.

- Please refer to 49 C.F.R. Section 192.9179(b) and referenced sections of ASME B318.S-2010 for a description of the records required under Subpart O.