QUESTION DAO12-1:

In a telephone call dated 2/2/12, Sempra used the term “Feature Studies” to describe how pipeline segments were selected for the PSEP.  Please define “Feature Studies” and explain the step-by-step process used to determine the segments proposed for hydro testing and for replacement in the PSEP for both SoCalGas and for SDG&E.

RESPONSE DAO12-1:

“Feature Studies” is a SoCalGas/SDGE specific term used to describe the gathering, integrating, and reviewing of pipeline data.  It refers to the evaluation of pipeline features and operating history through the records review process described in Section III of the April 15th, 2011 Report of Southern California Gas Company and San Diego Gas & Electric Company on Actions Taken in Response to NTSB Safety Recommendations.  A summary of that process is provided on page 6 of the Report as follows:

SoCalGas and SDG&E have reviewed established MAOPs for all pipelines that were not included in Categories 1, 2, or 3. During the course of their records search, the Utilities reviewed many types of pre-construction documents that provide confidence that the pipelines were manufactured, designed and constructed to operate safely. Such records include design and construction specifications and drawings, material specifications, pipe mill inspections and tests to eliminate manufacturing flaws prior to arrival at the construction site and other pre-construction documentation. Post-construction records (e.g., as-built drawings and records of strength tests) provide additional information to validate the integrity of a pipeline after installation.

Starting on page 49, our Testimony provides a full description of the process used to review the results of the records review to determine whether to identify a segment for proposed pressure testing or replacement.

QUESTION DAO12-2:

Please describe the database used to perform the “Feature Studies” and identify the data used for each line in the PSEP.

RESPONSE DAO12-2:

The records review referenced above are not the product of a database, but rather are the review of physical records as described in response DAO12-1.  The results of the records review are compiled into a summary spreadsheet which are used in conjunction with subject matter expert review to determine the outcomes in accordance with Figure IV-1 on page 61 of the Testimony.

The data used to identify each line (segment) to be addressed in the PSEP, and their final outcome is provided in Appendix IX-1-A through IX-1-D of the work papers supporting our Testimony.  Each workpaper provides the category designation (categories 1-4), segment length, and length meeting NTSB criteria.

QUESTION DAO12-3:

Please provide a copy of the data used in the “Feature Studies” for each line proposed in the PSEP for both SoCalGas and for SDG&E.

RESPONSE DAO12-3:

The actual data reviewed is voluminous.  The attached spreadsheet DRA_DAO_12-3 and the information provided in Appendices IX-1-A through IX-1-D of the workpapers supporting Chapter IX of the testimony provide a summary of the data reviewed during our records review process described in Response DAO 12-1.

QUESTION DAO12-4:

On page 61 of the testimony, Figure IV-1 shows the PSEP Decision Tree.  Please provide a copy of the data, database and/or application used to determine the outcome of all PSEP lines, as identified in Appendix IX-1-A (p.WP-IX-1-Ai), Appendix IX-1-B (p. WP-IX-1-Bi), Appendix IX-1-C (p. WP-IX-1-Ci), and Appendix IX-1-D (p. WP-IX-1-Di) as they are evaluated through the decision process.

RESPONSE DAO12-4:

The data used to determine the outcomes of all PSEP lines in accordance with Figure IV-1 is identified within each of the workpapers contained in Appendices IX-1-A through IX-1-D.

QUESTION DAO12-5:

Figure IV-1, Pipeline Safety Enhancement Plan Test/Replace Decision Tree, on page 61 shows a text box with the heading, “Sub-Prioritization Methodology”.  Please provide the following information with regard to the sub-prioritization methodology:

  - Please identify and describe the sub-prioritization methodology.

  - Please explain “scheduling priorities” and explain how each line, identified in Appendix IX-1-A (p.WP-IX-1-Ai), Appendix IX-1-B (p. WP-IX-1-Bi), Appendix IX-1-C (p. WP-IX-1-Ci), and Appendix IX-1-D (p. WP-IX-1-Di) is evaluated.

  - Please explain in detail the ranking system and identify the step-by-step process of how each line, as identified in Appendix IX-1-A (p.WP-IX-1-Ai), Appendix IX-1-B (p. WP-IX-1-Bi), Appendix IX-1-C (p. WP-IX-1-Ci), and Appendix IX-1-D (p. WP-IX-1-Di) was ranked.

  - Please identify the step-by-step evaluation process for each PSEP line, as identified in Appendix IX-1-A (p.WP-IX-1-Ai), Appendix IX-1-B (p. WP-IX-1-Bi), Appendix IX-1-C (p. WP-IX-1-Ci), and Appendix IX-1-D (p. WP-IX-1-Di) using the sub-prioritization methodology.

  - Please provide a copy of the data, database and/or application used to sub-prioritize each of the PSEP lines.

RESPONSE DAO12-5:

- The sub-prioritization methodology is described on pages WP-IV-2 and WP-IV-10 of the workpapers supporting Chapter IV of the testimony:

“Per the decision tree (Figure IV-1), these pipelines were arranged into one of five groups based upon the pipeline length, impacts to customers, and capability to be in-line inspected. The pipelines within each group were then sub-prioritized for project initiation purposes by the pipeline's potential impact radius (PIR) divided by a long seam factor. A pipeline's potential impact radius is calculated by squaring the diameter (inches) of the pipe and multiplying this value by the pipeline's MAOP (psig). The square root of this product is then multiplied by the constant 0.69 to provide the radius in feet. The formula is PIR= 0.69*square root of (MAOP*Diameter2). The longseam factor is identified in Title 49 CFR 192.113.  While these sub-prioritizations will be used to initiate projects, it is anticipated that many projects will be addressed in parallel to complete all Phase 1A work within the 4 year window.”

- The “scheduling priorities” refer to the numbered boxes in the decision tree that, per page 62 of the testimony, “represent an inventory of pipeline segments that share the same outcome.”  The worksheets showing the segment by segment pipeline detail in Appendices IX-1-A through IX-1-D identify the “Decision Tree Box” that each segment is organized into per the decision tree.

- See part (a) of this response for a description of the ranking system (sub-prioritization methodology).  Refer to pages WP-IV-1 through WP-IV-12 of the workpapers supporting Chapter IV of the testimony for each individual pipeline’s assigned sub-priority ranking per the aforementioned methodology.

- See part (c) of this response.

- Please refer to the attachment in Response DAO 12-3.