QUESTION DRA-DAO-25-01:

Exhibit Reference: Chapter IV, SoCalGas/SDG&E Prepared Testimony in R.11-02-019

And Chapter IX, Cost Workpapers

In DRA-DAO-17, Q.2, DRA asked Sempra to explain in detail why there is an inclusion of Distribution pipelines and Storage lines in the workpapers.  Sempra’s response is as follows:

D.11-02-019 requires “California natural gas transmission pipeline operators to prepare and file a comprehensive Implementation Plan to replace or pressure test all natural gas transmission pipeline in California that has not been tested or for which reliable records are not available.” (p. 18) As explained in Response 1, we applied the Department of Transportation definition of “transmission pipeline” in construing the Commission’s directive.

For each line identified as “SoCalGas Distribution” on page WP-IX-1-Bi, please (a) explain in detail why Sempra is including the Distribution pipelines and Storage lines in the PSEP.  Please (b) identify the specific sub-part of 49 CFR 102 that applies to each line on page WP-IX-1-Bi.

RESPONSE DRA-DAO-25-01:

- In Ordering Paragraph Three of D.11-06-017, the Commission ordered all California pipeline operators to file and serve “a proposed Natural Gas Transmission Pipeline Comprehensive Pressure Testing Implementation Plan (Implementation Plan) to comply with the requirement that all in-service natural gas transmission pipeline in California has been pressure tested in accord with 49 CFR 192.619, excluding subsection 49 CFR 192.619(c).”  SoCalGas and SDG&E interpret the Commission’s use of the term “transmission pipeline” in D.11-06-017 to refer to those pipelines that meet the United States Department of Transportation’s (DOT) definition of a transmission line.  The DOT definition of a Transmission line is “a pipeline, other than a gathering line, that: (1) Transports gas from a gathering line or storage facility to a distribution center, storage facility, or large volume customer that is not down-stream from a distribution center; (2) operates at a hoop stress of 20 percent or more of SMYS; or (3) transports gas within a storage field.”  Therefore, the proposed PSEP was developed to address all pipeline that meets this DOT definition of transmission line.

SoCalGas and SDG&E utilize FERC functional reporting to classify and record costs related to their pipeline system.  Therefore, the costs for operations and maintenance of our pipelines are recorded according to their FERC accounting definition, which may differ from the DOT definition.  The lines identified as “SDG&E Distribution” in the cited Workpaper are lines that are identified as distribution lines for accounting, operations and maintenance purposes, but meet the DOT definition of a transmission line for purposes of complying with the Commission’s directives in D.11-06-017.

- The scope of 49 CFR 192 is described in Section 192.1 as follows:

a) This part prescribes minimum safety requirements for pipeline facilities and the transportation of gas, including pipeline facilities and the transportation of gas within the limits of the outer continental shelf as that term is defined in the Outer Continental Shelf Lands Act (43 U.S.C. 1331).

Multiple subparts (A - O), either wholly or partially, apply to the pipelines listed on workpaper page WP-IX-1-Bi

QUESTION DRA-DAO-25-02:

Did Sempra use a written procedure or protocol to determine what is “sufficient documentation” to “satisfy the requirements of 49 CFR 192.616 (a)(b) or (d)”.  If no, please explain. If yes, please provide a copy of the procedure/protocol.

RESPONSE DRA-DAO-25-02:

SoCalGas/SDG&E interpret the question to intend to refer to 49 CFR 192.619 (a), (b) or (d), because the code referenced (49 CFR 192.616 (a)(b) or (d)) pertains to “public awareness.”

No, as explained on pages 50-51 of our Testimony, SoCalGas and SDG&E prioritized pipelines that do not have sufficient documentation of a strength test to 1.25 x MAOP to be addressed in Phase 1.   As further explained on page 51 of our Testimony, “In Phase 2, which is expected to run in parallel with and extend past the completion of Phase 1B, remaining transmission pipeline segments that do not have sufficient documentation to validate post-construction pressure tests to 1.25*MAOP and all other remaining transmission pipelines that have not been strength tested in accordance with the Commission’s directives in this Rulemaking will be addressed.”  The phrase “in accordance with the Commission’s directives in this Rulemaking” includes the Commission’s directive that “all in-service natural gas transmission pipeline in California has been pressure tested in accord with 49 CFR 192.619, excluding subsection 49 CFR 192.619 (c).”

As explained beginning on page six of our April 15th Report on Actions Taken in Response to NTSB Safety Recommendations, the threshold of 1.25*MAOP was selected based on the fact that this threshold is known to establish a margin of safety:

All pipelines are designed and specified to be constructed with materials that can operate at the MAOP plus a safety margin.  As explained in a 2007 technical report prepared for the United States Department of Transportation Office of Pipeline Safety, the primary purpose of a strength test is to establish that the pipeline does not contain any flaws that would pose a threat to the pipeline in operation either at or below MAOP:

One definition of a stable pipeline defect could be a defect that never threatens the integrity of a pipeline at any time during the useful life of the pipeline.  Basically, such a defect would have one essential characteristic: its failure stress level would always be higher than the maximum stress level (considering both hoop stress and longitudinal stress) experienced by the pipeline during its useful life.  Therefore, it would never cause the pipeline to fail. . . . Any manufacturing defect or imperfection that survives a pre-service hydrostatic test to 1.25 times the maximum allowable pressure (MAOP) is stable immediately after the test.  The reason is that by virtue of having survived the test, it is too small to fail at the MAOP that is only 80% of the test pressure.

QUESTION DRA-DAO-25-03:

At the start of Sempra’s decision tree, Box A  shows that Sempra uses the criteria of Class 3 or 4 location or High Consequence Area and not have documented pressure carrying capacity of >1.25*MAOP for all pipelines to be evaluated for the PSEP.  Please (a) explain the reason(s) the carrying capacity of > 1.25*MAOP was used, and (b) explain why this criteria meets the requirements of 49 CFR 192.619.

RESPONSE DRA-DAO-25-03:

- Please see Response DAO-25-2 above, as well as the discussion beginning on page six of our April 15th Report on Actions Taken in Response to the National Transportation Safety Board Safety Recommendations.

- The criteria were used to satisfy the Commission’s directives in Ordering Paragraphs Two and Three of D.11-06-017.  Ordering Paragraph Two requires pipeline operators to propose a plan that “start[s] with pipeline segments located in Class 3 and Class 4 locations and Class 1 and Class 2 high consequence areas, with pipeline segments in other locations given lower priority for pressure testing.”  Ordering Paragraph Three of D.11-06-017 requires that the proposed plan “must reflect a timeline for completion that is as soon as practicable, and include interim safety enhancement measures, including increased patrols and leak surveys, pressure reductions, prioritization of pressure testing for critical pipelines that must run at or near Maximum Allowable Operating Pressure values which result in hoop stress levels at or above 30% of Specified Minimum Yield Stress, and other such measures that will enhance public safety during the implementation period.”

QUESTION DRA-DAO-25-04:

For each of the segments of the 322 SoCalGas miles and 63 SDG&E miles identified as Category 4 NTSB Criteria miles, please create an Excel file that provides the information set forth below in choices i, ii, iii, and iv.  If a choice does not apply to a particular segment, please so state.

    - Segment has no traceable, verifiable, and complete documentation demonstrating a maximum allowable operating pressure established through prior hydrostatic testing.  Please identify the line number and segments and provide a citation to the PSEP workpapers.

    - Segment has documentation showing that a strength test was specified, but SoCalGas and SDG&E have not yet located direct verification that the test was completed.  Please identify the line number and segments and provide a citation to the PSEP workpapers.

    - Segment has documentation showing a strength test was performed, but does not currently meet the requirements of Subpart J.

    - Segment was identified as having no documentation and categorized as an NTSB Criteria Mile, but SoCalGas or SDG&E has since searched and found the documentation to verify the existence or completion of a test.

RESPONSE DRA-DAO-25-04:

- This request cannot be answered in the format requested.  As explained beginning on page nine of our April 15th Report on Actions Taken in Response to NTSB Safety Recommendations:

Although NTSB Safety Recommendation P-10-3 authorizes PG&E to “[u]se traceable, verifiable and complete records located by implementation of Safety Recommendation P-10-2 (Urgent) to determine the valid maximum allowable operating pressure, based on the weakest section of the pipeline or component to ensure safe operation,” SoCalGas and SDG&E did not validate the MAOP of any pipeline segments using the approach specified in Safety Recommendation P-10-3. In order to do so, SoCalGas and SDG&E believe they would need to affirmatively state that no pipeline materials other than those specified and documented in identified records were installed. That is, records must demonstrate, without fail, that no components of any portion of the pipeline segment were changed subsequent to the date of identified records, effectively requiring a perfect chain of document custody for pipelines that may have been installed over fifty years ago and that have been subject to many different document retention regulatory requirements.

This is a very difficult, if not infeasible, threshold to achieve, and such a process could not be completed within the time allotted for this report. SoCalGas and SDG&E believe it prudent to preliminarily and conservatively classify these pipelines as Category 4.  Both utilities therefore focused their efforts instead toward development of an action plan for all pipeline segments in Category 4.

In our Comments on the Proposed Decision Transferring Consideration of Pipeline Safety Enhancement Plan to the Triennial Cost Allocation Proceeding, we additionally stated the following:

The statement in the Proposed Decision that pipeline operators were required by federal regulations to maintain their records in accordance with the NTSB’s directives in the safety recommendations to PG&E is not accurate….

…the definition and applicability of the term “traceable, verifiable and complete” to the natural gas industry is currently under consideration by the Commission in the context of its review of Pacific Gas and Electric Company’s (PG&E) proposed Implementation Plan in this proceeding. The verification of records is also under consideration by PHMSA in response to the Pipeline Safety, Regulatory Certainty and Jobs Creation Act of 2011, signed into law January 3, 2012, and are anticipated to be considered in connection with the review of SoCalGas and SDG&E’s proposed Pipeline Safety Enhancement Plan in the Triennial Cost Allocation Proceeding. Indeed, PG&E has submitted evidence in this proceeding to establish that the term “traceable, verifiable and complete” was not used in the natural gas industry prior to the use of the term by National Transportation Safety Board in its January 3, 2011 safety recommendations to PG&E. As a result of the use of this phrase in the safety recommendations issued to PG&E, there is much debate and discussion of the issue currently taking place throughout the transmission pipeline industry as to how to define and apply this new standard.  Accordingly, SoCalGas and SDG&E seek clarification that this Proposed Decision does not predetermine this issue before SoCalGas and SDG&E have had an opportunity to present rebuttal testimony on this issue in the Triennial Cost Allocation Proceeding in support of their Proposed Pipeline Safety Enhancement Plan.

As noted in the quotes above, the term “traceable, verifiable and complete” is a term that, as far as SoCalGas and SDG&E are aware, was never used in the natural gas industry prior to the NTSB’s use of the term in its recommendations to PG&E.  Unless and until the phrase, “traceable, verifiable, and complete” has been defined and its applicability to the natural gas industry determined, SoCalGas and SDGE cannot provide responses that are referenced to or based upon this phrase.

- All segments that lack sufficient documentation of a pressure test to 1.25 x MAOP are characterized as Category 4 in the PSEP filing.  As noted on pages nine to ten in our April 15th Report on Actions Taken in Response to NTSB Safety Recommendations:

Many pipeline segments in Category 4 also have documentation showing that a strength test was specified. But SoCalGas and SDG&E have not yet located direct verification that the test was completed. For example, there is supporting documentation for approximately 15 Criteria Miles of Line 2003 that references a hydrostatic test procedure, as well as change orders to the construction contractor for hydrostatic testing of the pipeline. However, because explicit strength test records, such as recording charts or test logs, do not exist, and because the actual change orders have not yet been located, this pipeline segment is classified in Category 4.

As further explained on page 10 of our April 15th Report, “the evidence of test planning provides an additional degree of confidence in the safety of this pipeline and illustrates the conservative approach SoCalGas and SDG&E took in response to the NTSB recommendations.”  However, the need to separately group all segments with similar documentation histories was not deemed critical at the time of the records review, and the observations made are not compiled in any systematic fashion or available for reporting.  Identification of these segments in the format requested by DRA would require a manual review of the documentation amassed during the records review process, which would require considerable time, effort and resources.  If DRA wishes to schedule this extensive review and categorization, please contact our Case Manager, Jeff Salazar, to develop a schedule, which will necessarily have to be set for after the currently ongoing work that DRA has requested us to perform in response to other data requests is completed.

- The requirements of Subpart J do not apply to segments tested prior to 1970.  For any pre-1970 segments that do not have sufficient documentation of a pressure test to 1.25 x MAOP, the segment is identified as Category 4 in our PSEP.  As part of the response to DRA-DAO-16-06, the ratio of test pressure to MAOP will be provided and can be used to identify Category 4 segments that do have a documented strength test, but to a level less than 1.25 x MAOP.

- See the attached spreadsheet.

QUESTION DRA-DAO-25-05:

Please refer to DRA-DAO-17 Q. 10. DRA understands the response SoCalGas and SDG&E provided to this data request to mean that SoCalGas and SDG&E did not use any of the choices a through f to determine whether to include a segment in their proposed PSEP.  Please create an Excel file that provides the information set forth below in choices a, b, c, d, e, and f.  If a choice does not apply to a particular segment, please so state.

- Segment has no traceable, verifiable, and complete documentation demonstrating a maximum allowable operating pressure established through prior hydrostatic testing.  Please identify the line number and segments and provide a citation to the PSEP workpapers.

- Segment has documentation showing that a strength test was specified, but SoCalGas and SDG&E have not yet located direct verification that the test was completed.  Please identify the line number and segments and provide a citation to the PSEP workpapers.

- Segment was identified as having no documentation and categorized as an NTSB Criteria Mile, but SoCalGas or SDG&E has since searched and found the documentation to verify the existence or completion of a test.

- Segment has no traceable, verifiable, and complete documentation demonstrating a maximum allowable operating pressure established through prior hydrostatic testing but is located in non-HCA class 1 or 2, and is included in Phase 1A for “operational necessity and project efficiency”.

- Segment has traceable, verifiable, and complete documentation demonstrating a maximum allowable operating pressure established through prior hydrostatic testing, but does not currently meet the requirements of Subpart J, and is included in Phase 1A for “operational necessity and project efficiency”.

- Segment has traceable, verifiable, and complete documentation demonstrating a maximum allowable operating pressure established through prior hydrostatic testing (to Subpart J standards) and is included in Phase 1A for “operational necessity and project efficiency”.

RESPONSE DRA-DAO-25-05:

- Please refer to Response DRA-DAO-25-4i.

- Please refer to Response DRA-DAO-25-4ii.

- Please refer to Response DRA-DAO-25-4iv.

- Please refer to Response DRA-DAO-25-4i.

- Please refer to Response DRA-DAO-25-4i.

- Please refer to Response DRA-DAO-25-4i.

QUESTION DRA-DAO-25-06:

Please reconcile the 607 miles (246 for replacement and 361 for pressure testing) on page 5 of the testimony with the 620 miles (258 for replacement and 360 for pressure testing) on page 53 of the testimony.

RESPONSE DRA-DAO-25-06:

Please reference Response DRA-DAO-05-01 for reconciliation between Table I-1 on page 5 and Table IV-5 on page 53 of the Testimony.

# Footnotes

Final Report on Evaluating the Stability of Manufacturing and Construction Defects in Natural Gas Pipelines, April 16, 2007, prepared for the United States Department of Transportation Office of Pipeline Safety by John. F. Kiefner of Kiefner and Associates, with the Assistance of the Natural Gas Association of America, pp. 17-18.

Testimony, page 52.  Sempra’s definition of “Accelerated Miles”

Testimony, page 52.  Sempra’s definition of “Accelerated Miles”

Testimony, page 52.  Sempra’s definition of “Accelerated Miles”