QUESTION KCL3-1:

Lines 19 to 20 on Page 67 indicate that Sempra currently has over 200 ASVs and RCVs in operation.  How many of these are ASVs and how many are RCVs?  Are any of them located in HCA and/or class 3/class 4 locations?

RESPONSE KCL3-1:

Table DRA-KCL-3-1.1 provides the requested information.  Note that valves protecting pipeline segments located in high consequence areas themselves may be located outside of high consequence areas.  Therefore, in the table below we include more comprehensive information to indicate the number of ASV and RCV valves that currently protect high consequence areas in Class 3 and 4 locations.

Table DRA-KCL-3-1.1

| Description | Total Valve Count | Associated subset of valves protecting Class 3/4 and/or HCA pipeline segments at 5-20 miles. |
| --- | --- | --- |
| RCVs*residing in Class 3/4/HCA locations. | 39 | 39 |
| RCVs * residing outside Class 3/4/HCA locations | 34 | 17 |
| ASVs residing in Class 3/4/HCA Locations. | 79 | 79 |
| ASVs residing outside Class 3/4/HCA locations. | 115 | 62 |
| Under review. | 5 | 4 |
| Total | 272 | 201 |

*Does not include smaller RCVs associated with compressor station mode and internal operational controls.  Limited to valves directly associated with main pipeline operations.

QUESTION KCL3-2:

How many times have the ASVs and RCVs described above been activated because of a real pressure drop incident?  Please describe each incident in detail, including the pressures levels and final valve position (fully or partially closed).

RESPONSE KCL3-2 (Table DRA KCL-3-2 Amended 3/8/12 to include pressure files associated with incidents dated 7/11/2011 and 8/7/2010. No other Pressure data available – beyond data retention period.  Note each file shows the distance from the incident associated with each pressure measurement location.  Pressures (max, min and average) in all files shown as psig.)

Based on a fourteen-year period review, collectively, SoCalGas and SDG&E average roughly one event per year involving the closure of an ASV due to either legitimate operational pressure drops or other pipeline problems warranting closure.  The most recent activation of a linebreak control associated with a SoCalGas pipeline (Line 404) rupture is described on page 72 of our Testimony.

Table DRA-KCL-3-2 below chronicles the companies’ thirteen most recent major pipeline ruptures/gouge events which involved credible pressure excursions constituting ASV closure-for-cause.  In ten out of eleven instances where ASVs were installed within five miles of the rupture, and where the pressure drop parameters exceeded allowable limits, the valves fully closed, as-engineered. In one instance, a valve experienced partial closure.

Table DRA-KCL-3-2:

Added 3/8/12 – Files of closest available pipeline pressure recordings during the incident day, where available, are attached. Data includes max, min and average values for each hour. Red line entries in data files show incident hour.

| Date | Pipeline/Event | ASV#/state | ASV#/state |
| --- | --- | --- | --- |
| 7/10/2011 | L404 mp 28.48 rupture-farm equipment. Pressure data file attached 3/8/12-incident date revised. | MLV 404-20.81 /ASV fully-closed (1/1). | MLV 404-30.48/ASV fully-closed (2/2). |
| 8/7/2010 | L85/gouge-farm equipment. Pressure data file attached 3/18/12. | Manual valves closed | Manual valves closed |
| 2007 | L6001-2/ rupture.-bombed by military. Pressure Data Not Available (3/8/12). | Manual valves closed. | Manual valves closed |
| 2005 | L85/rupture-landslide Pressure Data Not Available (3/8/12). | Under review at document release. | Under review at document release. |
| 2/28/2005 | L324/rupture –landslide Pressure Data Not Available (3/8/12). | MLV 324-6/ASV fully-closed (3/3). | MLV 324-7/ASV fully-closed (4/4). |
| 12/11/2003 | L800 mp 5.14/gouge-farm equipment. Pressure Data Not Available (3/8/12). | Manual valves closed. | Manual valves closed |
| 2002 | L8109/ rupture-landslide. Pressure Data Not Available (3/8/12). | MLV 8109-18.08 ASV fully closed. (5/5) | MLV/Manually closed. |
| 1/16/2002 | L85/gouged-farm equipment. Pressure Data Not Available (3/8/12). | Manual valves closed. | Manual valves closed. |
| 2/2/2001* | L85/gouged-farm equipment. Pressure Data Not Available (3/8/12 –incident date refined). | Manual valves closed. | Manual valves closed |
| 3/2/98* | L406-mp 12.66/ rupture landslide. Pressure Data Not Available (3/8/12 –incident date revised). | MLV 404-12.48/ASV fully- closed (6/6). | MLV 404-19.39/valve manually closed. |
| 3/1/98 | L404-mp 13.63 /rupture/landslide. Pressure Data Not Available (3/8/12). | MLV 404-13.48/ASV fully-closed (7/7). | MLV 404-16.99/ASV fully- closed (8/8). |
| 2/17/98 | L1004-mp 31.58 /rupture-landslide. Pressure Data Not Available (3/8/12). | 1004-29.38/ASV fully-closed (9/9). | 34.18/ Manual valve closed at manned. station. |
| 2/14/98 | L404-mp 2.28/rupture-landslide/mp. Pressure Data Not Available (3/8/12). | 404-0.00/ASV partial-closure (9/10) | 404-3.71/ASV fully-closed (10/11). |

Table Note “mp”=pipeline milepost.

QUESTION KCL3-3:

How many times have the ASVs and RCVs described in KCL3-1 been activated because of a false alarm?  Please describe each incident in detail, including the pressures levels and final valve position (fully or partially closed).

RESPONSE KCL3-3 (Amended 3/8/12 to include pressure data files, where available, associated with each ASV incident. Note each file shows the distance from the incident associated with each pressure measurement location.   Pressures (max, min and average) in all files shown as psig) See Amended Response KCL 3-4 for RCV information:

Attached is a listing of 2011 spurious ASV closures and/or, where known, causes.  This information was extracted from operational logs. Year 2011 was a typical year with five events registered.

Date: 12/26/11

Incident: V4 (225-29.68 -0 ) Levelle Rd. Linebreak valve at Wheeler Ridge Compressor Station closed.  Controller experienced abnormal pressure readings.  Technician discovered valve closed and reopened it.  No indication as to why it closed.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 9/18/11

Incident: V18 (235-181.57-0) L-235 Linebreak valve near Adelanto compressor Station closed.  Controller experienced abnormal pressure readings.  Technician discovered valve closed and reopened it.  No indication as to why it closed.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 9/16/11

Incident: V12 (2000-125.13-0) L-2000 Linebreak valve at Whitewater Reg.  Station closed.  Controller experienced abnormal pressure readings.  Valve tripped due to line pressure swings caused by station regulation setup at Whitewater. Valve reopened.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 5/18/11

Incident: V4 (225-29.68-0) Levelle Rd. Linebreak valve at Wheeler Ridge Compressor Station closed.  Controller experienced pressure changes due to Wheeler Ridge compressor shutdown.  Valve reopened.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 3/26/11

Incident: V20 (2000-181.34-0) L-2000 Linebreak valve near Corona closed.  Controller experienced abnormal pressure readings.  Technician discovered valve closed and reopened it.  No indication as to why it closed.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

See edits to KCL-3-4 for pressures associated with RCV problems, where available.

QUESTION KCL3-4:

What is Sempra’s assessment on the reliability of its ASV systems and its RCV systems?  What is the probability (in percentage of being successful?) that either system will perform as anticipated when real emergency situations occur?  Please respond and provide documentations.

RESPONSE KCL3-4 (Amended 3/8/12 to include pressure data files, where available, associated with each RCV incident presented in this Response. Note each file shows the distance from the incident associated with each pressure measurement location. Pressures (max, min and average) in all files shown as psig):

ASVs:

The requested analytics are not compiled by SoCalGas or SDG&E as a normal course of operations.  We have only identified one instance in the last fourteen years where an ASV that was supposed to fully close based on pressure drop parameters failed to do so (a partial closure was experienced). On that basis, the empirical system Mean-Time-Between-Failure for closure-when-required could be calculated at 1/(365/24/194/14) or 25 Million hours.

However, a simple analysis of Table DRA-KCL-3-2 shows that of the eleven valves that should have fully closed due to ruptures over the fourteen-year period, one valve experience a partial closure.  Categorizing this partial closure as a failure would place the experienced reliability of closure when called upon to isolate a rupture at 91% over the fourteen-year period.

The larger issue for SoCalGas and SDG&E in terms of system reliability is the closure of a valve for reasons other than a pipeline rupture.  Such closures can potentially result in wide-scale customer outages if not properly planned for in base ASV system design. With five such instances chronicled in 2011, the mean-time-between failure for ASVs can logically and nominally be computed as 1/(5/365/24/194) or 339,888 hours.  This translates into a calculated reliability (CR) as follows:

CR=(1-(1/339,888 )*100=99.9%

RCVS:

The information below on RCV problems encountered in 2011 was extracted from operational logs.

Date: 12/11/11

Incident:  V8 (2000-155.06-8) at Moreno Reg. Station would not close.  Controller unable to operate valve remotely. Technician lubed valve to close and returned to service.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 11/3/11

Incident: V3 (3000-248.48-0) at Balboa Reg. Station not responding to set point control.  Controller unable to operate valve remotely.  Technician found valve stuck in closed position. Valve cycled and returned to service.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

Date: 11/1/11

Incident: V519-2 at Newberry Compressor Station not responding to commands.  Controller unable to operate valve remotely.  Technician found hydraulic leak.  Repairs made, valve returned to service.

Added 3/8/12 – File of closest available pipeline pressure recordings during the incident day is attached. Data includes max, min and average values for each hour.

In addition there were two valve station failures associated with electrical power surges and/or lightning strikes that compromised electronic controllers used to remotely control valves in 2011.  At two valves per station rendered inoperable for each incident, this brings the total count of RCVs that experienced some operational problem, when called upon for service, in 2011 to seven (7).  Assuming operations personnel averaged one control valve command function initiation per hour for the year, these seven failures translate into a composite reliability calculated as (1-7/365/24) or 99.94%.

QUESTION KCL3-5:

How did Sempra check the performances of the ASV/RCV systems when they were first installed?  Explain how and how frequently does Sempra check/activate the ASV/RCV systems to make sure they still work in the field over time?  Please respond and provide documentations.

RESPONSE KCL3-5:

SoCalGas and SDG&E test each base valve for operational integrity annually.

Beyond basic valve compliance-related testing, where electronic linebreak controls and PLCs are employed, these devices are also tested and inspected following installation and on an annual schedule thereafter to ensure power systems, pressure sensors, control systems, control gas regulators and logic programs are calibrated and/or functional.   To test base functionality, a known pressure drop (based on engineering calculations provided for a specific section of pipeline) is introduced to the sensor that monitors for a pre-set pressure drop threshold to activate a switch to drive the valve to close.  Operation is confirmed when that pressure drop results in positive control system closure activation. These tests are conducted outside of (in addition to) the basic overpressure protection system inspection protocols required by the CPUC.

A field instructional guideline on ASV inspection (“Line Guard Inspection instruction.doc”) is attached electronically.

QUESTION KCL3-6:

Does Sempra have any documented action plans in the event the ASVs/RCVs fail to perform during real emergencies?  Please provide such plans if they are available or explain if they are not available.

RESPONSE KCL3-6:

Closure (or non-closure) of an ASV or RCV are treated as any other high-priority operational call-outs that may have acute impacts on our ability to serve customers.  Gas Transmission field personnel are called directly and immediately after control room assessment that conditions warrant further action. Field personnel who monitor SCADA operations directly can also self-initiate an investigative dispatch.

SoCalGas Standard 223.0031 covers general transmission system Emergency and Abnormal Operating Condition protocols where the dispatch of field personnel is required.  This document is available for review/inspection at our Gas Control Center or other SoCalGas facility.

QUESTION KCL3-7:

Does Sempra have any documented reliability data on the performance of ASV/RCV from other pipeline operators in the US and around the world?  Please provide these data if they are available.

RESPONSE KCL3-7:

No.

QUESTION KCL3-8:

In the testimony, Sempra indicates that all the automatic valves will have both ASV and RCV capability.  Please explain what that statement means.  Will the valves be set to either ASV or RCV mode, or both modes simultaneously?  If both modes simultaneously, then please explain the operational sequence.

RESPONSE KCL3-8:

The planned valve controls can be set to provide for either mode of operation or both modes simultaneously.  Detailed analyses and operational histories for specific pipelines will ultimately determine which mode(s) will be activated at a given location.  And these designations may change over time, depending on lessons learned, changes in operational flow patterns and introduction of new customers and pipeline assets into the operational plan.  The expected configuration at most locations will be to provide the ASV functionality first, but also to enable operators to remotely control the same valves as conditions verified by enhanced control room diagnostics and/or field observations warrant.