QUESTION 15-1:

- Please provide a copy of each of the monthly reports that were submitted to the Commission’s Safety Enforcement Division, as referred to in the June 7, 2013, Motion of Southern California Gas Company and San Diego Gas & Electric Company to Continue Tracking Interim Pipeline Safety Enhancement Plan Costs in Authorized Memorandum Accounts.

RESPONSE 15-1:

Attached are monthly reports September 2012- April 2013 that have been submitted to the Commission.

QUESTION 15-2:

- Regarding the updated Attachment A to the Motion:

  - Please explain in detail the basis of the statement at Note 1: “Scope reduced as a result of our ongoing review of pipeline pressure test records.”

  - Regarding each of the pipeline projects listed separately in the updated Attachment A that are designated as having a “significant reduction in scope:”

    - Specifically, what information has become available as of June 7, 2013, that was not available as of January 13, 2012, when SoCalGas/SDG&E submitted their comments in response to the Assigned Commissioner’s Rulings, which presented a prioritized list of pipeline projects in the Supplement to Request for Memorandum Account Attachment A-SoCalGas and Attachment A-SDG&E?

    - Using the station stop and station start information that was presented in SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D, please designate each section of the pipeline that remains to be either pressure tested or replaced as of June 7, 2013.

    - Please state the cost estimate as of June 7, 2013, for the remaining Phase 1A work in terms of capital or O&M dollars.

  - Please explain in detail the basis of the statement at Note 2: “Scope no longer in Phase 1A.”

  - Regarding each of the pipeline projects listed separately in the updated Attachment A that are designated as having a “scope no longer in Phase 1A:”

    - Specifically, what information has become available as of June 7, 2013 that was not available on as of January 13, 2012?

    - As of June 7, 2013, does the scope of the project that SoCalGas/SDG&E state must be completed in Phase 2 remain the same as was described in the SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D?

    - If the answer to the previous question is “no,” then please describe the revised scope using the station stop and station start information that was presented in SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D.

    - If the answer to the question prior to the previous question is “yes,” does the June 7, 2013, cost estimate for the work to be completed in Phase 2 remain the same as was presented in the SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D?

    - If the answer to the previous question is “no,” please state the June 7, 2013 cost estimate for the Phase 2 work in terms of either capital or O&M dollars.

RESPONSE 15-2:

15.2.1	The statement “Scope reduced as a result of our ongoing review of pipeline pressure test records” indicates that the current estimate of the Phase 1A scope of the project is less than what was originally filed.  This is due largely to our review of post-construction pressure test records for those pipe segments resulting in portions of those segments no longer being prioritized for Phase 1A per our PSEP Decision Tree.

15.2.2.1	Since filing our Supplement to Request for Memorandum Account on January 13, 2012, SoCalGas and SDG&E have continued to review pressure test documentation and pipeline attribute information to refine and verify the scope for PSEP projects.  Records were also reviewed to comply with new requirements from PHMSA to validate pipeline MAOPs.  Information reviewed since January 13, 2012 has resulted in pipe segments either no longer being prioritized for Phase 1A per the PSEP Decision Tree or no longer being classified as DOT-defined Transmission.

15.2.2.2	The table below lists those lines in Attachment A that were noted as having a significant reduction in scope, and their associated remaining miles to be pressure tested or replaced as of June 7, 2013. The accelerated/incidental miles shown are estimates based on the remaining Category 4 Criteria Miles, and will be confirmed as detailed engineering, design, and execution planning is completed for these lines.

|  | Remaining Miles as of June 7, 2013 |
| --- | --- |
| Pipeline | Category 4 Criteria | Accelerated/ Incidental | Total |
| 2001 East 1 | - | - | - |
| 2001 West | 11.01 | 2.50 | 13.51 |
| 235 East 2 | - | - | - |
| 2003 | 0.03 | - | 0.03 |
| 407 | 1.04 | 0.25 | 1.29 |
| 406 | 0.74 | 0.70 | 1.44 |
| 235 West | 1.40 | - | 1.40 |
| 1013 | 0.02 | - | 0.02 |
| 1015 1 | - | - | - |
| 44-137 3 | 0.94 | 0.01 | 0.95 |
| 41-6000-2 | 4.94 | 0.30 | 5.24 |
| 31-09 | 1.23 | - | 1.23 |
| 37-04 4 | - | - | - |
| 35-10 4 | - | - | - |
| 38-200 5 | 0.28 | - | - |
| 36-8-01 4 | - | - | - |
| 38-512 | 0.13 | - | 0.13 |
| 41-05 4 | - | - | - |
| 38-552 4 | - | - | - |

- As of June 7, 2013, additional review of pressure test records has resulted in zero miles being prioritized for Phase 1A of the PSEP.

- As of June 7, 2013, the remaining mileage has been determined to no longer be in an HCA area, and therefore, no longer qualifies as Criteria Miles.

3	Initial analysis work on Line 44-137 indicates, with high probability, that the line can be pressure tested rather than replaced, as was initially determined.  A change from replacement to pressure testing Line 44-137 is expected to result in a significant cost reduction.  A detailed cost estimate for pressure testing this line has not yet been prepared.

4	As of June 7, 2013, the remaining mileage has been determined to have pipe specifications resulting in the pipe having hoop stress less than 20% SMYS at MAOP. Therefore, the miles no longer fall within the scope of our PSEP.

5	As of June 7, 2013, additional information on pipe specifications for this project has resulted in additional Category 4 Criteria Miles being placed within the scope of this line. This line no longer has a scope reduction.

15.2.2.3	New cost estimates for projects indicated as having “significant reduction in scope” have not yet been prepared as of June 7, 2013.  These estimates will be completed once aspects of the projects such as scope, execution plan, and schedule have been further developed.

15.2.3	The statement “Scope no longer in Phase 1A” indicates that the Phase 1A scope of the project as originally filed is now completely deferred to Phase 2 or removed from the PSEP altogether.  This is due largely to our ongoing review of post-construction pressure test records resulting in a determination that the pipe segments are either no longer prioritized for Phase 1A per our PSEP Decision Tree, or are reclassified as DOT Distribution.

15.2.4.1	See response to 15.2.2.1

15.2.4.2	For projects that are noted as having “scope no longer in Phase 1A”, the scope that is now determined to be deferred from Phase 1A to Phase 2 of the PSEP is the same as originally described in the SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D.

15.2.4.3	N/A

15.2.4.4	Until further information can be gathered, the cost estimates presented in the SoCalGas/SDG&E Amended PSEP Workpapers, Chapter IX, Appendices A-D for projects that are now entirely deferred from Phase 1A to Phase 2 remain the same.  As with all PSEP projects, costs will be updated as projects commence and detailed engineering, design, and execution planning are performed.

15.2.4.5	N/A