QUESTION DRA-DAO-26-01:

Regarding the statement on page 41 of the testimony, “When compared to pressure testing, TFI tools can provide equivalent detection capability for critically sized defects, and better detection capability for small defects…” please provide the following:

- the basis for this statement;

- Identify the top 25 sources Sempra relied on to reach this conclusion and provide a copy of these sources (hard and/or soft).

- A detailed explanation of why TFI has not been widely used by Sempra in its TIMP, DIMP or other pipeline assessment programs?

- Identify all TFI projects performed by SoCalGas or SDG&E and provide the assessment date, associated costs, the number of repairs made, and the cost of pipeline repairs associated with the TFI assessments.

- A copy of all “historical projects” relied on to support the ILI repair cost estimate presented on page WP-IX-1-40.

RESPONSE DRA-DAO-26-01:

- The detection capability of in-line inspection tools (including TFI) compared to pressure testing is related to the basic physics involved with the two assessment methods.  For a detailed primer on the comparative detection capabilities of TFI and pressure testing, please refer to the background information available starting on page 59 in the archived copies of the June 24, 2011 Educational Symposium on In-Line Inspection of Gas Pipelines located on the CPUC website at: http://www.cpuc.ca.gov/NR/rdonlyres/0DEA7BA4-5421-4287-BD32-A22863A2BFE9/0/INLINEINSPECTIONSYMPOSIUMCONCATENATEDFINAL.pdf .

- Please refer to Response DRA-DAO-15-03b.  The following references were utilized as part of both our April 15, 2011 Report on Actions Taken in Response to the National Transportation Safety Board Safety Recommendations, and as part of our PSEP:

- Baker, Michael Jr., in association with Kiefner and Associates, Inc., and CorrMet Engineering Services, PC, Low Frequency ERW and Lap Welded Longitudinal Seam Evaluation, TTO Number 5, Integrity Management Program Delivery Order DTRS56-02-D-70036 (2003), pp. 15-16, 31.

- Kiefer, John F., Maxey, Willard A., The Benefits and Limitations of Hydrostatic Testing (2000), p. 9.

Attachment Benefits&LimitsHydro.pdf

- ASME/ANSI B31.8.S-2010, Managing System Integrity of Gas Pipelines. This material is copyrighted.  SoCalGas and SDG&E cannot reproduce, but it is available at:http://www.asme.org/products/codes---standards/managing-system-integrity-of-gas-pipelines-%281%29

- PowerPoint Presentation titled: Application of Integrity Assessment, Michael J. Rosenfeld, Kiefner & Associates, Inc., presented at the Commission’s In-line Inspection Symposium, San Francisco, June 24, 2011.  Website link provided in previous responses to DRA, and included in Response DRA-DAO-26-01a.

- Final Report on Evaluating the Stability of Manufacturing and Construction Defects in Natural Gas Pipelines, April 26, 2007, prepared for the United States Department of Transportation Office of Pipeline Safety by John Kiefner of Kiefner and Associates, with the Assistance of the Natural Gas Association of America.  Provided to DRA in Response DRA-DAO-09-03.

Additionally, an internet search using the key search words “transverse, field, inspection” will provide more than 25 sources of information.

- As described on page 39 of our Testimony, SoCalGas and SDG&E perform assessments in accordance with the integrity management requirements contained in Federal regulations:

Current Federal regulations specify assessment, prevention and repair methods for all types of potential threats.  The assessment methods referenced in the current pipeline integrity regulations are direct assessment, pressure testing, and in-line inspection.  Each method has relative strengths and weaknesses, and is selected singularly or in combination depending upon the particular threat characteristics of the pipeline in question.

With respect to in-line inspection, to date, axial MFL tools have been satisfactory for compliance with these assessment requirements.

- Please see Response DRA-DAO-15-03c.  The response provided in DRA-DAO-15-03c includes costs for the repair of two sites.  Cost tracking is performed on a work order basis, and many costs are comingled.

The repairs from the TFI assessments took place from 10/27/11 – 12/22/11 and the pressure reduction was completed on 9/29/11. The total cost for the two repairs from the TFI assessment was $945,130.   The costs were broken down as follows:

·         Total capital charges of $793,796,

·         Total O&M charges of $151,333

- Response DRA-DAO-06 provides recent historical costs for repair activity.  A specific project or set of projects was not used for the estimated cost associated with post-ILI repair work.  Rather, subject matter expertise and institutional knowledge of previous repair work was applied to determine a reasonable, high-level allowance to include as part of the total cost of the TFI effort.  Every project contains unique circumstances that can affect both the scope and cost of these activities.

QUESTION DAO-26-2:

Identify and provide a copy of the top 25 sources Sempra relied on to determine that, “Non-Destructive examination offers an equivalent means to validate the strength of the pipeline segment.”

RESPONSE DAO-26-2:

See Response DRA-DAO-20-01d.  Additionally, an internet search using the key search words “non-destructive, testing, evaluation” will provide more than 25 sources of information.

QUESTION DAO-26-03:

Identify the cost savings that could be achieved—per mile and per year, compared to the proposed PSEP replacement and abandonment of short segments—if the Commission were to approve the use of the Non-Destructive Examination methods discussed on page 54 of the testimony.

RESPONSE DAO-26-03:

As stated on page 118 of our Testimony:

It is estimated that the integrity of approximately 1.64 miles of pipelines for SoCalGas and .05 miles for SDG&E covered in Phase 1 of this Pipeline Safety Enhancement Plan could be validated through Direct Examination more economically and with less system and customer impacts as compared to pressure testing or replacement.  Using direct examination methods in lieu of replacement or pressure testing on this mileage could reduce the Pipeline Safety Enhancement Plan costs by approximately $5-  15 million.  If this method is approved, SoCalGas and SDG&E would study additional areas to apply this method with the potential for additional cost savings.

We do not have an estimated cost reduction per-mile or per-year.  As noted in our Testimony quoted above, we would conduct further analysis to enhance potential cost savings if this method were approved by the Commission.